## Slide 1: BRX Technical Training
File System

## Slide 2: File System
Do-more Technology Version 2.0 added:
  RAM Drive File System (@RamFS)
    All Do-mores can support the FILE instructions with a firmware upgrade
    BRX supports this by default
    1 MB available system RAM
      Contents lost:
        If CPU is powered down
        If REBOOT instruction is executed
    Can have 512 entries (files and folders) in root folder
    Can have 3000 entries in each sub-folder
    Long file names supported but use up entry memory

## Slide 3: File System
Do-more Technology Version 2.0 added:
  SD Card File System (@SDCardFS)
    Only BRX supports
    Automatically created and mounted when the SD card is inserted
    The $SDCardFS.MediaInstalled and $SDCardFS.MediaMounted bits will be ON if there is a functional file system available
    Uses FAT32 formatted media
      Micro-SD card must be formatted in a PC before it can be used in a Do-more CPU
      This limits the size of SD card to 32GB
      Any media larger must be reformatted to FAT32
      SD cards formatted as NTFS or exFAT will not mount properly (MEM LED remains red)
    Same entry spec as @RamFS
Use utility program called Browse PLC File Systems manage the contents of the two file systems
  Browse contents of the folders
  Copy files between PLC & PC
  Delete files on the PLC
New EMAIL parameter allows the attachment of files from PLC’s file systems

## Slide 4: File System
Structure members
  .FolderEntryNum (unsigned word; RO) – number of file & subfolders found after scanning contents of folder; use with FILEQUERY
  .StartFolderScan (bit; R/W) – set ON to initiate a folder scan operation; use with FILEQUERY
  .FolderScanDone (bit; R/W) – ON at the completion of a folder scan operation; use with FILEQUERY
  .RemovableMedia (bit; RO) – ON if file system has a slot for removable media (e.g. micro SD slot)
  .MediaInstalled (bit; RO) – ON if media is installed (e.g. micro SD is plugged in)
  .MediaMounted (bit; RO) – ON if media is installed & mounted (e.g. micro SD card is installed & formatted)
  .FreeSpaceKB (signed doubleword; RO) – remaining number of KB of storage left on the file system
  .TotalSpaceKB (signed doubleword; RO) – number of KB of total usable storage

## Slide 5: File System
FILELOG “Log To File”
  Pick File System
  Input Leg
    Edge triggered
    Power flow enable
      Log Interval
  Append Timestamp to File Name – since this names the file, if “to the Day” is picked then when the day changes a new file is created with the new name
  Generate File Name – stores the current file name in a string for use with other instructions
  Entries:
    Up to 50 entries
    Count must be <= 10
    Date/Time prefixes every entry automatically
Store the current File Name in SS0 for convenience

## Slide 6: File System
FILELOG “Log To File” example

## Slide 7: File System
FILECOPY “Copy File”
  Simply copies a file
    This is where the Generate File Name parameter of the FILELOG instruction can come in handy

## Slide 8: File System
FILEDEL “Delete File”
  Simply deletes a file
    This is where the Generate File Name parameter of the FILELOG instruction can come in handy

## Slide 9: File System
FILENEWFLDR “Make New Folder”
  Creates a new folder

## Slide 10: File System
FILESYSCMD “Perform File System Command”
  Pick Command:
    Format – removes all files & folders on selected File System (only valid for @RamFS File System)
    Dismount – prepares the @SDCardFS File System media for extraction
      All open files will be closed
      Any outstanding file operations will complete
      MEM light on BRX CPU will turn red
    Mount – prepares the @SDCardFS File System for use
      MEM light on BRX CPU will turn green

## Slide 11: File System
FILEOPEN “Open File”
  Uses a File Handle Structure (e.g. FILE_0) which will be created if it doesn’t already exist, with the following members:
    .DeviceID (unsigned word; RO) – IDs this file handle
    .Open (bit; RO) – ON if file is open
    .Success (bit; RO) – (not used)
    .Error (bit; RO) – (not used)
    .EndOfFile (bit; RO) – ON if .FilePointer is at the end of the file
    .FileSize (signed Dword; RO) – number of bytes in file
    .FilePointer (signed Dword; RO) – current location being pointed to in the file
      Where FILEREAD, FILEWRITE & FILETRUNC operations will be executed

## Slide 12: File System
FILEOPEN “Open File” example
Use the File Name that was stored in SS0 from the previous example instead of having to type in the name manually

## Slide 13: File System
FILEREAD “Read from File”
  References a File Handle Structure (e.g. FILE_0)
  Exactly like a STREAMIN instruction
    Define delimiters
      If a FILELOG was used to create the lines in the file, then the delimiters will be:
        0x0D (carriage return)
        0x0A (line feed)
    Store the data in a string or numeric data block

## Slide 14: File System
FILEREAD “Read from File” example

## Slide 15: File System
FILECLOSE “Close File”
  References a File Handle Structure (e.g. FILE_0)
  Simply closes the file

## Slide 16: File System
FILEWRITE “Write to File”
  References a File Handle Structure (e.g. FILE_0)
  Exactly like a STREAMOUT instruction

## Slide 17: File System
FILEWRITE “Write to File” example
  I want to append a statement to the end of an already-existing file:
    “This is the end of file:” and then use the name of the file itself
      Use a STRPRINT with “This is the end of file:” SS0
  The key is to use FILEOPEN and open it as “Write (Create/Append if exists)”
    This will open the existing file and set the .FilePointer to the end of the file
      Thus .EndOfFile bit will be ON as well

## Slide 18: File System
FILESEEK “Seek to Position in File”
  References a File Handle Structure (e.g. FILE_0)
  File referenced must be already open
  To open to the end of a file, for example:
    Set Seek to = Beginning
    Set Positive offset from BEGINNING = FILE_0.FileSize
  Use this to point anywhere in a file

## Slide 19: File System
FILETRUNC “Truncate File”
  References a File Handle structure (e.g. FILE_0)
  Truncates an open file at the .FilePointer location
  Typical use:
    Open a file using FILEOPEN
    Use FILESEEK to set .FilePointer to the location in the file where the truncation is to happen
    Execute the FILETRUNC

## Slide 20: File System
FILEQUERY “Query File or Folder Information”
  Used for 3 main functions:
    Existence – check for the existence of a particular filename
    Information – gather any or all of 4 characteristics of a file or folder in a particular folder:
      Date
      Size
      Attributes
      Actual Name
    Iteration – gather any or all of the above 4 characteristics of all the files and folders in a particular folder

## Slide 21: File System
FILEQUERY “Query File or Folder Information”
  Existence
Checking for the existence of this File Name (SS0)
These parameters are not used when just checking for the existence of a file
If the File Name exists C128 will be ON
If the File Name does not exist C129 will be ON

## Slide 22: File System
FILEQUERY “Query File or Folder Information”
  Information (4 characteristics can be queried)
    File Date – when the file was last written to, in 1970 Epoch format (number of seconds since January 1, 1970)
    File Size in Bytes
    File Attributes – double word defined as:
      Bit0 – ON = read only (cannot be modified)
      Bit1 – ON = hidden (cannot be seen)
      Bit2 – ON = system file (cannot be modified)
      Bit3 – ON = volume label (name of the file is the file system’s volume name created when the file system was formatted)
      Bit4 – ON = directory (folder; the Query File/Folder Name entry is a folder, not a file)
      Bit5 – ON = archive (bit is set ON when the file is created or when it is modified)
      Bits 6-31 – Not used
    Actual File Name – string, fully qualified file name as stored in the file system
<Bits 6-31 not used>
5
4
3
2
1
0
Archive
Folder
Volume
System
Hidden
Read Only

## Slide 23: File System
FILEQUERY “Query File or Folder Information”
  Information (4 characteristics can be queried)
All of these parameters are optional

## Slide 24: File System
FILEQUERY “Query File or Folder Information”
  Iteration (4 characteristics can be queried) – the iteration query is executed manually using structure members of the file system
    For each characteristic queried, create a unique block of memory to store the information
      e.g. Block of 256 strings to store the FileNames
      e.g. Block of 256 signed DWords to store FileDates
      e.g. Block of 256 signed DWords to store FileSizes
      e.g. Block of 256 signed DWords to store FileAttributes
    Clear those blocks (e.g. MEMCLEAR)
    Set .StartFolderScan bit ON
    Reset .FolderScanDone bit OFF
    Zero out Iteration Index parameter chosen in the FILEQUERY instruction
    Execute the FILEQUERY instruction
      This will store the characteristics in the blocks above for ONE file/folder found and then increment the Iteration Index parameter in preparation for next query
    If no more files/folders exist in the folder, then .FolderScanDone bit will be ON indicating FILEQUERY should not be executed again
    If .FolderScanDone bit is still OFF, then the FILEQUERY can be executed again to get the next set of characteristics for the next file/folder
    See Help file for excellent example of iteration using Stages