## Slide 1: BRX Technical Training
High-Speed I/O (PWM Outputs)

## Slide 2: High-Speed I/O
BX10
  6 discrete IN (all high-speed)
  4 discrete OUT (2 high-speed)
  No analog IN
  No analog OUT
  No Ethernet port
BX10E
  6 discrete IN (all high-speed)
  4 discrete OUT (2 high-speed)
  1 analog IN
  1 analog OUT
  Ethernet port

## Slide 3: High-Speed I/O
BX18
  10 discrete IN (all high-speed)
  8 discrete OUT (4 high-speed)
  No analog IN
  No analog OUT
  No Ethernet port
BX18E
  10 discrete IN (all high-speed)
  8 discrete OUT (4 high-speed)
  1 analog IN
  1 analog OUT
  Ethernet port

## Slide 4: High-Speed I/O
BX36
  20 discrete IN (10 high-speed)
  16 discrete OUT (8 high-speed)
  No analog IN
  No analog OUT
  No Ethernet port
BX36E
  20 discrete IN (10 high-speed)
  16 discrete OUT (8 high-speed)
  4 analog IN
  2 analog OUT
  Ethernet port

## Slide 5: High-Speed Outputs (PWM Outputs)
PWM = Pulse Width Modulation

## Slide 6: High-Speed Outputs (PWM Outputs)
Select Device Name & Output
Use Structure Members to control the PWM Output
.EnableOutput (bit; R/W) – set ON to generate pulses; OFF to stop
.PeriodScale (bit; R/W) – if OFF the .Period is in microseconds; if ON, milliseconds
.Period (unsigned word; R/W) – 0 to 65,535 micro- or milliseconds
.DutyCycle (real; R/W) – percentage of the .Period the pulse will be ON; 0.0 to 100.0%