## Slide 1: Do-more Technical Training
CTRIO2
(Introduction)

## Slide 2: Instruction Set
THE BASICS
  181 instructions
    Contact (14)
    Coil/Bit Output (11)
    Analog/Process (13)
    Date/Time/Calendar (7)
    Ethernet (5)
    Hardware/Device (9)
    High Speed/CTRIO (19)
    Math (5)
    Misc/Data Manipulation (23)
    Program Control (20)
    Program-Looping (8)
    Protocol-Custom/ASCII (7)
    Protocol-Standard (10)
    String (14)
    Timer/Counter/Drum (16)

## Slide 3: Instruction Set
THE BASICS
  181 instructions
    In-line (100) – no flag
      Executes completely in-line on same scan
    Fully Asynchronous (48) – Red
      Dependent on shared Device’s availability
      Locks Device when executed to make it exclusive
      Unlocks Device after it is finished
      Must not terminate before it is finished
      Must wait for Success or Error indication
      All CTRIO2 instructions are fully asynchronous
    Multi-scan (20) – Yellow
      Takes 2 or more scans to complete or function properly
      Depend on the status of the instruction from previous scan
      (Edge-triggering inputs normally take 2 also)
    Yielding (5) – Blue
      Can temporarily postpone operation until next scan
    Skipping (6) – Green
      Can skip forward or backward in code
    Yielding/Skipping (2) - Blue Green
      Can temporarily postpone operation until next scan and skip forward or backward in code
Box Instruction
Corner

## Slide 4
High Speed/CTRIO (19)
  CTAXCFG – CTRIO2 Axis Configuration
  CTAXDYNP – CTRIO2 Axis Run Dynamic Position Mode
  CTAXDYNV – CTRIO2 Axis Run Dynamic Velocity Mode
  CTAXJOG – CTRIO2 Axis Jog Mode
  CTAXLIMT – CTRIO2 Axis Run Trapezoid w/Limits
  CTAXTRAP – CTRIO2 Axis Run Trapezoid
  CTDYNPOS – CTRIO Run Dynamic Position Mode
  CTDYNVEL – CTRIO Run Dynamic Velocity Mode
  CTPLSADD – CTRIO2 Add Entry to PLS
  CTPLSEDT – CTRIO2 Edit PLS Entry
  CTREGRD – CTRIO Read Register
  CTREGWR – CTRIO Write Register
  CTRUNPOS – CTRIO Run Position Mode
  CTRUNVEL – CTRIO Run Velocity Mode
  CTTBLADD – CTRIO Add Entry to Preset Table
  CTTBLCLR – CTRIO Clear Table
  CTTBLEDT – CTRIO Edit Preset Table Entry
  CTTBLLD – CTRIO Load Table
  CTUPDLVL – CTRIO Update Level
CTRIO2 – Introduction

## Slide 5: CTRIO2 – Introduction

## Slide 6: CTRIO2 – Introduction
Flash (ROM)
  DL-PLC: memory where CTRIO Workbench configuration is stored
  Do-more: irrelevant
Runtime RAM
  DL-PLC: on power-up Flash (ROM) is copied to here
  Do-more: overwrites whatever is here with the Module Configuration stored in the Do-more
Active RAM (0-3): memory where the active Table for each Pulse Output is stored
Table #0: Special Table that is always active

## Slide 7: CTRIO2 – Introduction
DL-PLC
CTRIO2
ROM
RAM
CTRIO Workbench
CWB File
CTRIO Configuration #1
CTRIO Configuration #1
CTRIO Configuration #1
A CTRIO configuration is created in CTRIO Workbench software
The configuration is written to CTRIO RAM & then copied to ROM
CTRIO Configuration #1
A copy must also be stored in a CWB file in case the CTRIO2 ever needs replacement

## Slide 8: CTRIO2 – Introduction
DL-PLC
CTRIO2
ROM
RAM
CTRIO Workbench
CWB File
CTRIO Configuration #1
When everything is powered down, the configuration only exists in the CWB file (if saved!) and the ROM of the CTRIO2
CTRIO Configuration #1
If the CTRIO2 is replaced for any reason then the configuration would be lost if not previously saved in the CWB file
If the configuration was previously saved in the CWB file, then it can be read up into CTRIO Workbench and written back to the new CTRIO2
CTRIO Configuration #1
CTRIO Configuration #1
CTRIO Configuration #1

## Slide 9: CTRIO2 – Introduction
DL-PLC
CTRIO2
ROM
RAM
CTRIO Workbench
CWB File
CTRIO Configuration #1
CTRIO Configuration #1
CTRIO Configuration #1
POWER = OFF
POWER = ON
On power up the CTRIO2 copies the configuration from ROM to RAM
The DL-PLC works with the RAM copy because it is much faster, of course

## Slide 10: CTRIO2 – Introduction
CTRIO2
ROM
RAM
Do-more
Do-more Designer
CTRIO Configuration #2
A CTRIO configuration is created in Do-more Designer in the System Configuration  Module Configuration
System Config
CTRIO Configuration #2
The configuration is written to the System Configuration (Flash Memory)
CTRIO Configuration #2
The configuration is also written to the CTRIO2’s RAM
The configuration is never written to the CTRIO2’s ROM
Do-more Project
A copy is also stored in the Do-more Project file
CTRIO Configuration #2

## Slide 11: CTRIO2 – Introduction
CTRIO2
ROM
RAM
Do-more
Do-more Designer
System Config
CTRIO Configuration #2
POWER = OFF
POWER = ON
CTRIO Configuration #2
On power up the Do-more copies the configuration from System Configuration to CTRIO2 RAM
Do-more Project
CTRIO Configuration #2

## Slide 12: CTRIO2 – Introduction
CTRIO2
ROM
RAM
Do-more
Do-more Designer
System Config
CTRIO Configuration #2
POWER = OFF
POWER = ON
CTRIO Configuration #1
CTRIO Configuration #1
CTRIO Configuration #2
Do-more Project
CTRIO Configuration #2
On power up the CTRIO2 copies the configuration from ROM to RAM
However, that copy will get overwritten by the Do-more on power up
Thus, if this same CTRIO2 was placed in a DL-PLC it would have configuration #1; if in a Do-more it would have configuration #2
Also, if the CTRIO2 was to be replaced there is no need to reconfigure it because on power up the Do-more writes the proper configuration down to the CTRIO2

## Slide 13: CTRIO2 – Introduction
CTRIO2
1A
1B
1C
1D
2A
2B
2C
2D
0
1
2
3
I
N
P
U
T
S
O
U
T
P
U
T
S
Ch 1
Ch 2