## Slide 1: Do-more Technical Training
Communications
(DirectLOGIC)

## Slide 2: Communications – DirectLOGIC
DL Server (Slave)
  (1) Do-more built-in Ethernet port
  (2) Do-more w/ECOM100
DL Client (Master)
  (1) Do-more built-in Ethernet port
  (2) Do-more w/ECOM100
Client (Master)
Server (Slave) #1

## Slide 3: Communications – DirectLOGIC
DL Server (Slave)
  (1) Do-more’s DL Server Device exists & is enabled by default but is invisible & not configurable
  (2) ECOM100’s DL Server is also not configurable
  Both have a Module ID parameter so both broadcasting & peer-to-peer comms function the same
  Both serve up DL-memory to the DL Client
    C-bits (C) 0-177777  DLC0-177777*
    Inputs (X) 0-177777  DLX0-177777*
    Outputs (Y) 0-177777  DLY0-177777*
    V-memory (V) 0-177777  DLV0-177777*
      *Range is expandable in Do-more via Memory Configuration

## Slide 4: Communications – DirectLOGIC
DL Client (Master)
  (1) Do-more’s DL Client Device exists (@IntEthernet) & is enabled by default
    Use Device Configuration to change parameters as desired:
      ACK Timeout: how long to wait for an ACK from partner
      Command Timeout: how long to wait for partner to respond to a data request
      Retries
  (2) ECOM100’s DL Client
    Use NetEdit3’s Advanced Settings or the ECOM100’s web interface to change parameters as desired:
      ACK Timeout: (same as above)
      Resp. Timeout: (same as Command Timeout above)
      Retries
  Both use DLRX (Read) & DLWX (Write) instructions
  Both can use Broadcasting to Module ID, or peer-to-peer via IP address
  Both use UDP/IP (connectionless comms)
Client (Master)
Server (Slave) #1

## Slide 5: Communications – DirectLOGIC
DL & ECOM History Lesson
  Objective: Establish Ethernet communications between DL-CPUs
  Stipulation: “Take the Ethernet-ness out of the equation”
  Enter ECOM/ECOM100 modules
    Actually the first ones were called “ENET” modules
DL-PLC
DL-PLC
Ethernet
Switch
IP Addr: 10.1.1.150
IP Addr: 10.1.1.155
Data Exchange

## Slide 6: Communications – DirectLOGIC
DL & ECOM History Lesson
  Requirements:
    Ethernet requires IP Addresses (double-word)
      Can communication be established without them?
        Yes, via broadcasting & raw Ethernet II packets
    DL-PLC has limited instructions to communicate over backplane to intelligent modules
      SP-Busy bit for the slot (SP122)
      1st LD:
        Base #: 0
        Slot #: 1
        Partner’s Module ID: 14
      2nd LD: number of bytes to read: 8 (4 words)
      LDA: storing of the data after the read (V2000-2003)
      RX: what to read from the partner (V3000-3003)
    Module ID (a number from 0-90) is the only means to address the communication partner

## Slide 7: Communications – DirectLOGIC
DL & ECOM History Lesson
  ECOM Design:
    Module must have Module ID address
    To “remove Ethernet-ness” the Module ID must be settable via a dipswitch
    ECOMs must be able to “find” one another without IP Addresses
      Broadcasting will be utilized for this

## Slide 8: Communications – DirectLOGIC
DL & ECOM History Lesson
  Solution:
    Customer removes new ECOMs from box
    Customer sets dipswitches to preferred Module IDs
    Customer plugs ECOMs into desired slots
    Customer figures out SP-Busy (& SP-Error) bit for the slot of the “master” (or “initiator”)
    Customer writes LD, LD, LDA, RX/WX rung in ladder logic in the “master”
    Master ECOM uses Ethernet II Broadcast with embedded HAP (Host Application Protocol) to ask who has Module ID
    Slave ECOM responds: “That’s my Module ID”
      Response telegram has slave ECOM’s MAC address
    Master ECOM utilizes the slave’s MAC address & uses regular Ethernet II telegrams with embedded HAP data to communicate
NOTE:
No “Ethernet-ness” knowledge required
No configuration software required (i.e. NetEdit)

## Slide 9: Communications – DirectLOGIC
DL & ECOM History Lesson
  Problem:
    Network administrators don’t like broadcast telegrams on their network
    ECOMs won’t communicate across bridges, routers and some managed switches because broadcasting is blocked
    How to get rid of broadcasting?
      Module ID (the only means to address the partner) must be translated to an IP address
      No way to do this without putting the “Ethernet-ness” back into the ECOM
      ECOMs must now have IP addresses
      A tool is needed to give ECOMs an IP address

## Slide 10: Communications – DirectLOGIC
DL & ECOM History Lesson
  The “No-broadcast” Solution:
    Customer removes new ECOMs from box
    Customer plugs ECOMs into desired slots (dipswitches are left at zero)
    Customer uses NetEdit to give ECOMs IP addresses
    Customer uses NetEdit to create Peer-to-peer table
    Customer figures out SP-Busy (& SP-Error) bit for the slot of the “master” (or “initiator”)
    Customer writes LD, LD, LDA, RX/WX rung in ladder logic in the “master”
    “Master” ECOM translates the Module ID in the 1st LD instruction into the IP address of the Partner ECOM
    “Master” ECOM generates a standard UDP telegram with embedded HAP data to communicate
NOTE:
“Ethernet-ness” knowledge required
Configuration software required (i.e. NetEdit)
However, problem solved: No broadcast telegrams
Notice in the old ECOM there is no Subnet Mask, nor Gateway Address
Translates a Module ID (3) to an IP Address (10.0.0.105)

## Slide 11: Communications – DirectLOGIC
DL & ECOM History Lesson
  New Advancements:
    ECOM100 invented
      Runs at 100Mbps
      Supports Modbus TCP (Client & Server)
        A 3rd-party TCP/IP stack is utilized to keep from “reinventing the wheel”
        TCP/IP requires Subnet Mask, and Gateway Address

## Slide 12: Communications – DirectLOGIC
DL & ECOM History Lesson
  New Advancements:
    DirectSOFT IBoxes invented
      Requires DipSwitch #7 on ECOM100s to be ON
      No need to figure out the correct SP bits because the ECOM100 IBox does that for you
      No need to figure out the LD, LD, LDA & RX/WX parameters because the ECRX/ECWX IBoxes do that for you

## Slide 13: Communications – DirectLOGIC
@IntEthernet DL Client (Master) Module ID: 1 IP Addr: 10.0.0.101
DO-MORE PLC
DL Server (Slave) Module ID: 5 IP Addr: 10.0.0.105
DO-MORE PLC
or
DL-PLC
DLRX/DLWX to Slave ID: 5
Eth II Broadcast
Eth II HAP-ACK
Eth II HAP-Data
This is a “Directed” Broadcast looking for Module ID: 5
Broadcasts are heard by every device on network. Routers & some switches block broadcasts

## Slide 14: Communications – DirectLOGIC
@IntEthernet DL Client (Master) Module ID: 1 IP Addr: 10.0.0.101
DO-MORE PLC
DL Server (Slave) Module ID: 5 IP Addr: 10.0.0.105
DO-MORE PLC
Or
DL-PLC
DLRX/DLWX to IP Addr: 10.0.0.105
UDP HAP-Request
UDP HAP-ACK
UDP HAP-Data

## Slide 15: Communications – DirectLOGIC
ECOM100 DL Client (Master) Module ID: 1 IP Addr: 10.0.0.101
(no Peer-to-peer)
DO-MORE
w/ECOM100
DL Server (Slave) Module ID: 5 IP Addr: 10.0.0.105
DO-MORE PLC
or
DL-PLC
DLRX/DLWX to Slave ID: 5
Eth II Broadcast
Eth II HAP-ACK
Eth II HAP-Data
This is a “Directed” Broadcast looking for Module ID: 5
Broadcasts are heard by every device on network. Routers & some switches block broadcasts
Notice when the Network Device is an ECOM100 (“@ECOM_006”) the Fixed IP Address & Variable IP Address parameters are greyed out

## Slide 16: Communications – DirectLOGIC
ECOM100 DL Client (Master) Module ID: 1 IP Addr: 10.0.0.101
Peer-to-peer
Module ID 3  IP Addr: 10.0.0.105
DO-MORE PLC
w/ECOM100
DL Server (Slave) Module ID: 5 IP Addr: 10.0.0.105
DO-MORE PLC
or
DL-PLC
DLRX/DLWX to Slave ID: 3
UDP HAP-Request
UDP HAP-ACK
UDP HAP-Data
With ECOM100 as Network Device in DLRX/DLWX only Slave ID is available
ECOM100’s Peer-to-peer Table translates the Slave ID of the DLRX/DLWX to an IP Address in a UDP telegram
The DL Server’s (Slave) Module ID: 5 is irrelevant for this transaction

## Slide 17: Communications – DirectLOGIC
DLRX “DirectLOGIC Network Read”
  Reads data from a DL Server (Slave)
  Fully asynchronous instruction (red triangle)
  Parameters:
    Network Device – e.g. @IntEthernet or @ECOM_003
    Remote Address
      Slave ID – corresponds to Module ID of DL Server (Slave) device
      Fixed IP Address – only available for @IntEthernet
      Variable IP Address – <ditto>
    From DL – DirectLOGIC memory type & offset (octal)
    Number of Bytes
    To – where read data is stored

## Slide 18: Communications – DirectLOGIC
DLRX “DirectLOGIC Network Read”
  Parameters:
    Enable
      Once on Leading Edge
      Continuous on Power Flow at Interval – executes multiple times based on the Interval configured
        Constant
        Variable
      On Success: Set bit or JMP to Stage
      On Error: Set bit or JMP to Stage

## Slide 19: Communications – DirectLOGIC
DLWX “DirectLOGIC Network Write”
  Writes data to a DL Server (Slave)
  Fully asynchronous instruction (red triangle)
  Parameters:
    Network Device – e.g. @IntEthernet or @ECOM_003
    Remote Address
      Slave ID – corresponds to Module ID of DL Server (Slave) device
      Fixed IP Address – only available for @IntEthernet
      Variable IP Address – <ditto>
    From – where data-to-be-written is located
    Number of Bytes
    To DL – DirectLOGIC memory where data is to be written

## Slide 20: Communications – DirectLOGIC
DLWX “DirectLOGIC Network Write”
  Parameters:
    Enable
      Once on Leading Edge
      Continuous on Power Flow at Interval – executes multiple times based on the Interval configured
        Constant
        Variable
      On Success: Set bit or JMP to Stage
      On Error: Set bit or JMP to Stage

## Slide 21: Communications – DirectLOGIC
Do-more CPU
DLRX
DLWX
EthII
@IntEthernet
Do-more CPU
DLC
DLX
DLY
DLV
DL Server
DirectLOGIC Client (Master)
DirectLOGIC Server (Slave)
EthII
Do-more CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
DL-CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
V, X, Y, C, S, T, CT, GX, GY, SP
Do-more CPU
DLRX
DLWX
@IntEthernet
DirectLOGIC Client (Master)
DLC
DLX
DLY
DLV
@ECOM_001
EthII
Do-more CPU
DLRX
DLWX
@IntEthernet
DirectLOGIC Client (Master)
Module ID
Module ID
Module ID
Currently does not work, instead the Do-more NAKs the request

## Slide 22: Communications – DirectLOGIC
Do-more CPU
DLRX
DLWX
UDP
@IntEthernet
Do-more CPU
DLC
DLX
DLY
DLV
DL Server
DirectLOGIC Client (Master)
DirectLOGIC Server (Slave)
UDP
Do-more CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
DL-CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
V, X, Y, C, S, T, CT, GX, GY, SP
Do-more CPU
DLRX
DLWX
@IntEthernet
DirectLOGIC Client (Master)
DLC
DLX
DLY
DLV
@ECOM_001
UDP
Do-more CPU
DLRX
DLWX
@IntEthernet
DirectLOGIC Client (Master)
IP Address
IP Address
IP Address

## Slide 23: Communications – DirectLOGIC
Do-more CPU
DLRX
DLWX
EthII
@ECOM_001
Do-more CPU
DLC
DLX
DLY
DLV
DL Server
DirectLOGIC Client (Master)
DirectLOGIC Server (Slave)
EthII
Do-more CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
DL-CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
V, X, Y, C, S, T, CT, GX, GY, SP
DLC
DLX
DLY
DLV
@ECOM_001
EthII
E
C
O
M
1
0
0
Do-more CPU
DLRX
DLWX
@ECOM_001
DirectLOGIC Client (Master)
E
C
O
M
1
0
0
Do-more CPU
DLRX
DLWX
@ECOM_001
E
C
O
M
1
0
0
DirectLOGIC Client (Master)
Module ID
Module ID
Module ID
Currently does not work

## Slide 24: Communications – DirectLOGIC
Do-more CPU
DLRX
DLWX
UDP
@ECOM_001
Do-more CPU
DLC
DLX
DLY
DLV
DL Server
DirectLOGIC Client (Master)
DirectLOGIC Server (Slave)
UDP
Do-more CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
DL-CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
V, X, Y, C, S, T, CT, GX, GY, SP
DLC
DLX
DLY
DLV
@ECOM_001
UDP
E
C
O
M
1
0
0
Peer
To
Peer Config
Do-more CPU
DLRX
DLWX
@ECOM_001
DirectLOGIC Client (Master)
E
C
O
M
1
0
0
Peer
To
Peer Config
Do-more CPU
DLRX
DLWX
@ECOM_001
DirectLOGIC Client (Master)
E
C
O
M
1
0
0
Peer
To
Peer Config
Module ID
Module ID
Module ID

## Slide 25: Communications – DirectLOGIC
DL-CPU
ECRX
ECWX
EthII
Do-more CPU
DLC
DLX
DLY
DLV
DL Server
DirectLOGIC Client (Master)
DirectLOGIC Server (Slave)
EthII
Do-more CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
DL-CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
V, X, Y, C, S, T, CT, GX, GY, SP
DLC
DLX
DLY
DLV
@ECOM_001
EthII
E
C
O
M
1
0
0
Module ID
DL-CPU
ECRX
ECWX
DirectLOGIC Client (Master)
E
C
O
M
1
0
0
Module ID
DL-CPU
ECRX
ECWX
DirectLOGIC Client (Master)
E
C
O
M
1
0
0
Module ID
Currently does not work

## Slide 26: Communications – DirectLOGIC
DL-CPU
ECRX
ECWX
E
C
O
M
1
0
0
Peer
To
Peer Config
UDP
Do-more CPU
DLC
DLX
DLY
DLV
DL Server
DirectLOGIC Client (Master)
DirectLOGIC Server (Slave)
UDP
Do-more CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
DL-CPU
DirectLOGIC Server (Slave)
E
C
O
M
1
0
0
V, X, Y, C, S, T, CT, GX, GY, SP
DLC
DLX
DLY
DLV
@ECOM_001
UDP
Module ID
DirectLOGIC Client (Master)
DirectLOGIC Client (Master)
DL-CPU
ECRX
ECWX
E
C
O
M
1
0
0
Peer
To
Peer Config
Module ID
DL-CPU
ECRX
ECWX
E
C
O
M
1
0
0
Peer
To
Peer Config
Module ID

## Slide 27: Communications – DirectLOGIC
# | Master CPU | Ethernet Port | Instruction | Device | Protocol
1 | Do-more | Internal | DLRX/DLWX (Module ID) | @IntEthernet | Broadcast Ethernet II
2 |  |  | DLRX/DLWX (IP Address) |  | UDP
3 |  | ECOM100 | DLRX/DLWX (Module ID) | @ECOM_001 | Broadcast Ethernet II
4 |  | ECOM100 (Peer-to-Peer) |  |  | UDP
5 | DL-PLC | ECOM100 | ECRX/ECWX (Module ID) | n/a | Broadcast Ethernet II
6 |  | ECOM100 (Peer-to-Peer) |  |  | UDP

## Slide 28: Communications – DirectLOGIC
# | Slave CPU | Ethernet Port | Protocol | Device | Memory Available
1 | Do-more | Internal | Broadcast Ethernet II* | @IntEthernet | DL-memory
2 |  |  | UDP |  | 
3 |  | ECOM100 | Broadcast Ethernet II | @ECOM_001 | 
4 |  |  | UDP |  | 
5 | DL-PLC |  | Broadcast Ethernet II | n/a | V, X, Y, C, S, T, CT, GX, GY, SP
6 |  |  | UDP |  | 
* - Currently (as of May-2016) does not work