## Slide 1: Do-more Technical Training
Communications
(Do-more)

## Slide 2: Communications – Do-more
RX “Do-more Network Read”
  Reads data from another Do-more PLC
  Fully asynchronous instruction (red triangle)

## Slide 3: Communications – Do-more
RX “Do-more Network Read”
  Parameters
    Device - @IntEthDMPPClient
    UDP Addressing  IP Address
        Fixed IP Address / Variable IP Address
        UDP Port Number
    Remote Password (optional)
      Text / Variable
    Enable
      Once on Leading Edge
      Continuous on Power Flow at Interval
        Constant / Variable
    On Success
      Set bit / JMP to Stage
      On Success Counter (optional)
    On Error
      Set bit / JMP to Stage
      On Error Counter (optional)
    Extended Error Information (optional)

## Slide 4: Communications – Do-more
RX “Do-more Network Read”
  Parameters
    Will not allow incorrect parameters
    Allows User Data Blocks!
    NOTE: Cannot read Heap Items
If User Data Block is chosen, then the “Data Block #” must be used to point to the block in the other Do-more PLC
The “Data Block #” is found in the other PLC via PLC  System Configuration  Memory Configuration

## Slide 5: Communications – Do-more
WX “Do-more Network Write”
  Writes data to another Do-more PLC
  Fully asynchronous instruction (red triangle)
  Parameters are exactly the same as the RX instruction

## Slide 6: Communications – Do-more
Do-more CPU
RX
WX
UDP
@IntEthDMPPClient
Do-more CPU
Memory Blocks
(no Heap)
DMPP Server
Do-more Peer-to-peer
Do-more Peer-to-peer