## Slide 1: Do-more Technical Training
Communications
(GS-EDRV100)

## Slide 2: Communications – GS-EDRV100
Use as slave with Do-more Ethernet I/O
Serially connects to drive
Works with:
  GS1
  GS2
  GS3/DURAPulse
LEDs
  STA – connected to drive
  SPD – 100Mbps Ethernet
  TXD – serial send
  ERR – fatal error
  LK/A – link / activity Ethernet
  RXD – serial receive
Dipswitches set Module ID
Use NetEdit or Do-more Designer to set IP parameters

## Slide 3: Communications – GS-EDRV100
System Configuration  CPU Configuration
Check “Enable Ethernet I/O Master”
Under I/O Configuration, click on the new “Ethernet I/O Master” that showed up

## Slide 4: Communications – GS-EDRV100
I/O Configuration
  Ethernet I/O Master
    Ethernet Master Address Configuration
      Set Node and IP Configuration
    Ethernet Slaves
      Set Slave IP Config…
        Setup Selected Slave
        Query Slaves
      Add Multiple Slaves via Query…
    Adds Module Configuration
    Adds Device that uses a Structure
Notes: Configure Ethernet I/O with your EBC100 slave

## Slide 5: Communications – GS-EDRV100
$GS2_100 Structure Members
  OutputFrequency (word)
  OutputCurrent (word)
  ExtCommFault (bit): drive serial
  IntCommFault (bit): Ethernet
  StatusMonitor1 (word): 2100 hex mem in drive
  StatusMonitor2 (word): 2101 hex mem in drive
  RunCommand (word): P9.27; 1 = Run; 0 = Stop
  RS485SpeedRef (word): P9.26; set speed
  Direction (bit): P9.28; ON = forward
  ResetCommFault (bit): turn ON to reset fault
  BlockParm1-5 (word): P9.11-.15; user-defined write value
  BlockParm6-15 (word): P9.16-.25; user-defined read value

## Slide 6: Communications – GS-EDRV100
GSREGRD “GS EDrive Register Read”
  Reads data from GS-EDRV100 (up to 50 read operations)
  Fully asynchronous
  Parameters:
    Device – GS-EDRV100
    Structure – structure being used
    Register – drive register to read from
      Press the <Insert> button to pull up all the selections
    Destination – where the read value is stored
    On Success / On Error: Set bit or JMP to Stage

## Slide 7: Communications – GS-EDRV100
GSREGWR “GS EDrive Register Write”
  Writes data to GS-EDRV100 (up to 50 write operations)
  Fully asynchronous
  Parameters:
    Device – GS-EDRV100
    Structure – structure being used
    Source – where write value originates
    Register – drive register to write to
      Press the <Insert> button to pull up all the selections
    On Success / On Error: Set bit or JMP to Stage