## Slide 1: Do-more Technical Training
Communications
(Modbus RTU)

## Slide 2: Communications – Modbus RTU
Modbus RTU Server (Slave)
  (1) Do-more built-in serial port
  (2) Do-more w/SERIO
Modbus RTU Client (Master)
  (3) Do-more built-in serial port
  (4) Do-more w/SERIO
Client (Master)
Server (Slave) #1

## Slide 3: Communications – Modbus RTU
Modbus RTU Server (Slave)
  (1) Do-more built-in serial port
    Modbus RTU Server (Slave) must be configured
      Use CPU Configuration  Serial Port Mode and select “Modbus RTU Server (Slave)”
      Use <Device Settings> button to change parameters as desired
      Configuration creates IntSerialServer structure with members:
        ActiveSessions – (unsigned byte) Not used
        LastError – (unsigned byte) Error code of last failed transaction
        Errors – (unsigned word) Number of failed transactions
        Transactions – (signed double-word) Number of successful transactions
    Function Codes Supported:
      1-7, 15, 16, 22
    Serves up M-memory to the Modbus RTU Client (Master)
      Modbus Inputs 0-1023  MI0-1023*
      Modbus Coils 0-1023  MC0-1023*
      Modbus Input Registers 0-2047  MIR0-2047*
      Modbus Holding Registers 0-2047  MHR0-2047*
      *Range is expandable via Memory Configuration

## Slide 4: Communications – Modbus RTU
Modbus RTU Server (Slave)
  (2) Do-more CPU with local SERIO/4 module
    Modbus RTU Server (Slave) must be configured
      Use Module Configuration(s), double-click on SERIO/SERIO4 module
      Select “Modbus RTU Server (Slave)” for the port you want to use
      Use <Device Settings> button for any of the 3 ports to change parameters as desired
      Configuration creates, e.g. $SERIO_001_A structure with members:
        ActiveSessions – (unsigned byte) Not used
        LastError – (unsigned byte) Error code of last failed transaction
        Errors – (unsigned word) Number of failed transactions
        Transactions – (signed double-word) Number of successful transactions
    Function Codes supported:
      1-7, 15, 16, 22
    Serves up M-memory to the Modbus RTU Client (Master)
      Modbus Inputs 0-1023  MI0-1023*
      Modbus Coils 0-1023  MC0-1023*
      Modbus Input Registers 0-2047  MIR0-2047*
      Modbus Holding Registers 0-2047  MHR0-2047*
      *Range is expandable via Memory Configuration

## Slide 5: Communications – Modbus RTU
Modbus RTU Client (Master)
  (3) Do-more built-in serial port
    Modbus RTU Client (Master) must be configured
      Use CPU Configuration  Serial Port Mode and select “Modbus RTU Client (Master)”
      Use <Device Settings> button to change parameters as desired
        Timeout: milliseconds (ms) to wait for Server (Slave) to respond
        Retries: how many times to retry comm
        Inter-packet Delay: time between packets
          This should be at least 3.5 character times
            (3.5 * (#BitsPerCharacter/Baud))*1,000,000
    Use MRX (Read) & MWX (Write) instructions
      Multiple MRX/MWX instructions can be used to same Server (Slave)
@IntSerModbusClient (Master)
Server (Slave) #1
Server (Slave) #2

## Slide 6: Communications – Modbus RTU
Modbus RTU Client (Master)
  (4) Do-more CPU with local SERIO/4 module
    Modbus RTU Client (Master) must be configured
      Use Module Configuration(s), double-click on SERIO/SERIO4 module
      Select “Modbus RTU Server (Slave)” for the port you want to use
      Use <Device Settings> button for any of the 3 ports to change parameters as desired
        Timeout: milliseconds (ms) to wait for Server (Slave) to respond
        Retries: how many times to retry comm
        Inter-packet Delay: time between packets
          This should be at least 3.5 character times
            (3.5 * (#BitsPerCharacter/Baud))*1,000,000
    Use MRX (Read) & MWX (Write) instructions
      Multiple MRX/MWX instructions can be used to same Server (Slave)

## Slide 7: Communications – Modbus RTU
@IntSerModbusClient Client (Master)
@IntSerial
Server (Slave) #1
MRX/MWX to 1
Modbus Request
ACK
Modbus Response
If Server does not respond in Timeout period it Retries the number of times specified before MRX/MWX instruction errors out
ACK

## Slide 8: Communications – Modbus RTU
MRX “Modbus Network Read”
  Reads data from a Modbus (TCP or RTU) Server
  Fully asynchronous instruction (red triangle)
  Parameters:
    Device – Modbus RTU Client Device name
    Unit ID – default 1
    Function Code
      1 (Read Coil)
      2 (Read Discrete Inputs)
      3 (Read Holding Registers)
      4 (Read Input Registers)
      7 (Read Exception Status
    From Modbus Offset Address
    Number of Modbus… “Coils”, “Discrete Inputs”, “Registers”
    To Do-more Memory Address – where received data is stored

## Slide 9: Communications – Modbus RTU
MRX “Modbus Network Read”
  Parameters:
    Enable
      Once on Leading Edge
      Continuous on Power Flow at Interval – executes multiple times based on the Interval configured
        Constant
        Variable
    On Success: Set bit or JMP to Stage
    On Error: Set bit or JMP to Stage
    Exception Response (optional)

## Slide 10: Communications – Modbus RTU
MWX “Modbus Network Write”
  Writes data to a Modbus (TCP or RTU) Server
  Fully asynchronous instruction (red triangle)
  Parameters:
    Device – Modbus RTU Client Device name
    Unit ID – default 1
    Function Code
      5 (Write Single Coil)
      6 (Write Single Register)
      15 (Write Multiple Coils)
      16 (Write Multiple Registers)
    To Modbus Offset Address
    Number of Modbus… “Coils”, “Registers”
    From Do-more Memory Address – where data to be written is stored

## Slide 11: Communications – Modbus RTU
MWX “Modbus Network Write”
  Parameters:
    Enable
      Once on Leading Edge
      Continuous on Power Flow at Interval – executes multiple times based on the Interval configured
        Constant
        Variable
    On Success: Set bit or JMP to Stage
    On Error: Set bit or JMP to Stage
    Exception Response (optional)

## Slide 12: Communications – Modbus RTU
Do-more CPU
MRX
MWX
@IntSerModbusClient
Do-more CPU
MC
MI
MIR
MHR
@IntSerial
Modbus RTU Client (Master)
Modbus RTU Server (Slave)
SERIO/4
Do-more CPU
MRX
MWX
@SERIO_001_A
Do-more CPU
MC
MI
MIR
MHR
@SERIO_001_A
Modbus RTU Client (Master)
Modbus RTU Server (Slave)
SERIO/4