## Slide 1: Do-more Technical Training
Communications
(Modbus TCP)

## Slide 2: Communications – Modbus TCP
Modbus TCP Server (Slave)
  (1) Do-more built-in Ethernet port
  (2) Do-more w/ECOM100
Modbus TCP Client (Master)
  (3) Do-more built-in Ethernet port
  (4) Do-more w/ECOM100
Client (Master)
Server (Slave) #1

## Slide 3: Communications – Modbus TCP
Modbus TCP Server (Slave)
  (1) Do-more built-in Ethernet port
    Modbus TCP Server Device exists & is enabled by default (see CPU Configuration)
      Use CPU Configuration  Modbus/TCP Server Configuration to change parameters as desired
        Maximum Concurrent Sessions: 1-16 (default 4)
          Up to 16 Clients (Masters) can talk to the Do-more. The 17th one will be unable to connect
        Client Inactivity Timeout: 1-65,535 seconds
          If Do-more hasn’t heard from one of his Clients (Masters) in this time period, Do-more will do a TCP disconnect
        TCP Port Number: default 502
    Serves up M-memory to the Modbus TCP Client
      Modbus Inputs 0-1023  MI0-1023*
      Modbus Coils 0-1023  MC0-1023*
      Modbus Input Registers 0-2047  MIR0-2047*
      Modbus Holding Registers 0-2047  MHR0-2047*
      *Range is expandable via Memory Configuration
Do-more SLAVE

## Slide 4: Communications – Modbus TCP
Modbus TCP Client (Master)
  (3) Do-more built-in Ethernet port
    One Modbus TCP Client Device (@IntModTCPClient) exists by default
      Use Device Configuration to change parameters as desired
        Timeout: milliseconds (ms) to wait for Server (Slave) to respond
        Retries: how many times to retry comm
        Inactivity Timeout: seconds to keep TCP connection alive due to inactivity (no MRX/MWX being executed) before doing a TCP disconnect from the Server (Slave)
    Use MRX (Read) & MWX (Write) instructions
      Multiple MRX/MWX instructions can be used to same Server (Slave)
    If >1 Server (Slave), create a Modbus TCP Client Device for each one (explained in a few minutes)…
Do-more MASTER

## Slide 5: Communications – Modbus TCP
DL & ECOM100 History Lesson
  Remember the New Advancements?:
    ECOM100 invented that runs at 100Mbps & supports Modbus TCP (Client & Server) requiring TCP/IP to be supported:
      IP address, subnet mask & gateway address
      Also, peer-to-peer must be used to select Modbus TCP
    New Problem: How to further select Modbus Function Code & register address?
DL-PLC w/ECOM100 MASTER

## Slide 6: Communications – Modbus TCP
DL & ECOM100 History Lesson
  Original Requirements:
    Module ID (a number from 0-90) is the only means to address the communication partner
      Solved with peer-to-peer table
  New Requirements:
    How to select Modbus TCP?
      SOLUTION: A 2nd peer-to-peer selection
    How to select Modbus FC?
    How to select register address?
    These last two are solved with mapping
Converts Module ID (“RX/WX Device Number”) to an IP Address
Not only converts Module ID (“RX/WX Device Number”) to an IP Address but also selects Modbus TCP protocol
DL-PLC w/ECOM100 MASTER

## Slide 7: Communications – Modbus TCP
DL & ECOM100 History Lesson
  Modbus TCP Client Mapping:
    Uses RX/WX operand to select both the Modbus FC & the register address
DL-PLC w/ECOM100 MASTER

## Slide 8: Communications – Modbus TCP
DL & ECOM100 History Lesson
  Modbus TCP Server Mapping:
    Responds to the Modbus FCs as shown
    Notice, however, FC03 & FC04 both serve up DL-PLC’s V-memory
      This is not usually a problem for 3rd-party Modbus TCP Clients, but…
DL-PLC w/ECOM100 SLAVE

## Slide 9: Communications – Modbus TCP
DL & ECOM100 History Lesson
  New Problem:
    Modbus TCP Client mapping doesn’t allow the ability to address Modbus Input Registers!
    SOLUTION: Use an odd length designation to change from using Holding Registers to using Input Registers
      Why this works: the length parameter is always an even number because it designates bytes and all Modbus registers are words (2 bytes)
IR?
DL-PLC w/ECOM100 MASTER

## Slide 10: Communications – Modbus TCP
DL & ECOM100 History Lesson
  All previous maps were for DL PLCs using ECOM100s
  Can ECOM100 be used to do Modbus TCP while in a Do-more PLC base?... Yes… however…
    To an ECOM100 as any kind of server in a Do-more PLC, only DL-memory is available
    So the server mapping chart is further restricted
      As Modbus TCP Server:
        FC01 “Read Coils”, FC05 “Force Single Coil” & FC15 “Force Multiple Coils” only access DLY0-1777 & DLC0-3777
        FC02 “Read Inputs” only accesses DLX0-1777
        FC03 “Read Holding Registers”, FC06 “Preset Single Register” & FC16 “Preset Multiple Registers” only access DLV0-7777
        FC04 “Read Input Registers” also only accesses DLV0-7777
    As Modbus TCP Client:
      Must use DLRX/DLWX (not MRX/MWX!) with proper parameter
DL-PLC w/ECOM100 SLAVE/MASTER

## Slide 11: Communications – Modbus TCP
Modbus TCP Server (Slave)
  (2) Do-more with ECOM100
    Do-more’s Modbus TCP Server is not utilized
    A Modbus TCP Server exists & is enabled in the ECOM100
    Modbus I/O mapping from ECOM100 will go to DL-memory
      Modbus Inputs:
        2049-3072  DLY0-1777*
        3073-5120  DLC0-3777*
      Modbus Coils:
        2049-3072  DLX0-1777*
      Modbus Input Registers:**
        1-4096  DLV0-7777*
        17,501-17,506  Internal ECOM100 Version Info (ECOM manual)
        17,511-17,600  Internal ECOM100 Device Data (ECOM manual)
      Modbus Holding Registers:**
        1-4096  DLV0-7777*
        18,001-18020  Internal ECOM100 Dynamic Mod Data (ECOM manual)
      * These ranges are larger than the default. Use Memory Configuration to enlarge them if needed
      ** Notice both Input & Output Registers address DLV
Do-more w/ECOM100 SLAVE

## Slide 12: Communications – Modbus TCP
Modbus TCP Client (Master)
  (4) Do-more with ECOM100
    Do-more’s Modbus TCP Client is not utilized
    A Modbus TCP Client exists & is enabled in the ECOM100
      Must configure a Peer-to-peer table and select Modbus TCP
    Must use DLRX/DLWX instructions with the proper From DL/To DL parameters
    DLRX with From DL parameter will select the following:
      FC01 “Read Coils” (Coils 1-6656):
        GY0-3777  1-2048
        Y0-1777  2049-3072
        C0-3777  3073-5120
        S0-1777  5121-6144
        T0-377  6145-6400
        CT0-377  6401-6656
      FC02 “Read Inputs” (Inputs 1-3584):
        GX0-3777  1-2048
        X0-1777  2049-3072
        SP0-777  3073-3584
      FC03 “Read Holding Registers” (HRs 1-17056):
        V0-41237  1-17056
      FC04 “Read Input Registers” (IRs 1-17056):
        V0-41237  1-17056*
    DLWX with To DL parameter will select the following:
      FC15 “Force Multiple Coils”: Same mapping as FC01 “Read Coils” above
      FC16 “Preset Multiple Registers”: Same mapping as FC03 “Read Holding Registers” above
      *To select this one requires the use of an odd number for the Number of Bytes parameter
Do-more w/ECOM100 MASTER

## Slide 13: Communications – Modbus TCP
@IntModTCPClient (Master)
DO-MORE PLC
Modbus TCP Server (Slave) #1
SYN
SYN, ACK
ACK
Modbus Request
ACK
Modbus Response
ACK
Establish TCP Connection #1 over Port #502
Modbus Protocol Exchange
MRX/MWX #1
TCP Connection #1 Established
TCP Connection #1 Established
If Server does not respond in 15 seconds (not configurable) the MRX/MWX instruction errors out
If Server does not respond in Timeout period it Retries the number of times specified before MRX/MWX instruction errors out
Do-more MASTER

## Slide 14: Communications – Modbus TCP
@IntModTCPClient (Master)
DO-MORE PLC
Modbus TCP Server (Slave) #1
Modbus Request
ACK
Modbus Response
ACK
Modbus Protocol Exchange
MRX/MWX #1
TCP Connection #1 Established
TCP Connection #1 Established
After TCP Connection is established, if an MRX/MWX is not executed within Inactivity Timeout setting, the TCP Connection is closed
Do-more MASTER

## Slide 15: Communications – Modbus TCP
@IntModTCPClient (Master)
DO-MORE PLC
Modbus TCP Server (Slave) #1
Modbus Request
ACK
Modbus Response
ACK
Modbus Protocol Exchange
MRX/MWX #1
TCP Connection #1 Established
TCP Connection #1 Established
Do-more MASTER

## Slide 16: Communications – Modbus TCP
@IntModTCPClient (Master)
DO-MORE PLC
Modbus TCP Server (Slave) #1
Modbus TCP Server (Slave) #2
FIN, ACK
FIN, ACK
ACK
Establish TCP Connection #2 over Port #502
TCP Connection #1 Established
TCP Connection #1 Established
MRX/MWX #2
Close TCP Connection #1
SYN
SYN, ACK
ACK
TCP Connection #2 Established
TCP Connection #2 Established
2nd Server (Slave) is added, but still using just one Modbus TCP Client in Do-more
TCP Connection to Server (Slave) #1 is still established
Do-more MASTER

## Slide 17: Communications – Modbus TCP
@IntModTCPClient (Master)
DO-MORE PLC
Modbus TCP Server (Slave) #1
Modbus TCP Server (Slave) #2
Modbus Request
ACK
Modbus Response
ACK
MRX/MWX #2
TCP Connection #2 Established
TCP Connection #2 Established
Do-more MASTER

## Slide 18: Communications – Modbus TCP
@IntModTCPClient (Master)
@MyModTCPClient (Master)
DO-MORE PLC
Modbus TCP Server (Slave) #1
Modbus TCP Server (Slave) #2
Modbus Request
ACK
Modbus Response
ACK
TCP Connection #1 Established
TCP Connection #1 Established
MRX/MWX #1
SYN
SYN, ACK
ACK
Establish TCP Connection #1 over Port #502
2nd Modbus TCP Client is created to service the 2nd Server (Slave) #2
Do-more MASTER

## Slide 19: Communications – Modbus TCP
@IntModTCPClient (Master)
@MyModTCPClient (Master)
DO-MORE PLC
Modbus TCP Server (Slave) #1
Modbus TCP Server (Slave) #2
Modbus Request
ACK
Modbus Response
ACK
Establish TCP Connection #2 over Port #502
TCP Connection #1 Established
TCP Connection #1 Established
MRX/MWX #2
SYN
SYN, ACK
ACK
TCP Connection #2 Established
TCP Connection #2 Established
No disconnect & reconnect (management) of the TCP Connections is necessary
MRX/MWX #1
MRX/MWX #1
MRX/MWX #1
MRX/MWX #2
MRX/MWX #2
MRX/MWX #2
Multiple MRXs & MWXs possible
Do-more MASTER

## Slide 20: Communications – Modbus TCP
MRX “Modbus Network Read”
  Reads data from a Modbus (TCP or RTU) Server
  Fully asynchronous instruction (red triangle)
  Parameters:
    Device – Modbus TCP Client Device name
    Modbus/TCP addressing
      IP Address
        Fixed Address
        Variable Address
      TCP Port Number – default 502
    Unit ID – default 255 (most Slaves ignore)
    Function Code
      1 (Read Coil)
      2 (Read Discrete Inputs)
      3 (Read Holding Registers)
      4 (Read Input Registers)
      7 (Read Exception Status
    From Modbus Offset Address
    Number of Modbus… “Coils”, “Discrete Inputs”, “Registers”
    To Do-more Memory Address – where received data is stored
Do-more MASTER

## Slide 21: Communications – Modbus TCP
MRX “Modbus Network Read”
  Parameters:
    Enable
      Once on Leading Edge
      Continuous on Power Flow at Interval – executes multiple times based on the Interval configured
        Constant
        Variable
    On Success: Set bit or JMP to Stage
    On Error: Set bit or JMP to Stage
    Exception Response (optional)
Do-more MASTER

## Slide 22: Communications – Modbus TCP
MWX “Modbus Network Write”
  Writes data to a Modbus (TCP or RTU) Server
  Fully asynchronous instruction (red triangle)
  Parameters:
    Device – Modbus TCP Client Device name
    Modbus/TCP addressing
      IP Address
        Fixed Address
        Variable Address
      TCP Port Number – default 502
    Unit ID – default 255 (most Slaves ignore)
    Function Code
      5 (Write Single Coil)
      6 (Write Single Register)
      15 (Write Multiple Coils)
      16 (Write Multiple Registers)
    To Modbus Offset Address
    Number of Modbus… “Coils”, “Registers”
    From Do-more Memory Address – where data to be written is stored
Do-more MASTER

## Slide 23: Communications – Modbus TCP
MWX “Modbus Network Write”
  Parameters:
    Enable
      Once on Leading Edge
      Continuous on Power Flow at Interval – executes multiple times based on the Interval configured
        Constant
        Variable
    On Success: Set bit or JMP to Stage
    On Error: Set bit or JMP to Stage
    Exception Response (optional)
Do-more MASTER

## Slide 24: Communications – Modbus TCP
Do-more CPU
MRX
MWX
ECOM100
@IntModTCPClient
Do-more CPU
MC
MI
MIR
MHR
@ModbusTCPServer
Modbus TCP Client (Master)
Modbus TCP Server (Slave)
Do-more CPU
MRX
MWX
@IntModTCPClient
Modbus TCP Client (Master)
Do-more CPU
DLC
DLX
DLY
DLV
DL Server
Modbus TCP Server (Slave)

## Slide 25: Communications – Modbus TCP
Do-more CPU
DLRX
DLWX
ECOM100
@ECOM_001
Do-more CPU
MC
MI
MIR
MHR
@ModbusTCPServer
Modbus TCP Client (Master)
Modbus TCP Server (Slave)
Do-more CPU
DLC
DLX
DLY
DLV
DL Server
Modbus TCP Server (Slave)
E
C
O
M
1
0
0
Modbus
Peer
to
peer
Do-more CPU
DLRX
DLWX
@ECOM_001
Modbus TCP Client (Master)
E
C
O
M
1
0
0
Modbus
Peer
to
peer

## Slide 26: Communications – Modbus TCP
# | Master CPU | Ethernet Port | Instruction | Device | Function Codes
1 | Do-more | Internal | MRX/MWX | @IntModTCPClient | 1-7, 15, 16
2 |  | ECOM100 (Modbus TCP Peer-to-Peer) | DLRX/DLWX1 | @ECOM_001 | 1-4, 15, 16
3 | DL-PLC |  | ECRX/ECWX2 | n/a | 
1 Must use Client table in “ECOM100 Server Client Mapping (Do-more).PDF” file to choose correct Function Code & Modbus memory address
2 Must use Client table in “ECOM100 Server Client Mapping.PDF” file to choose correct Function Code & Modbus memory address

## Slide 27: Communications – Modbus TCP
1 Must use Server table in “ECOM100 Server Client Mapping (Do-more).PDF” file to see where a Function Code & Modbus memory address maps into DL-memory
2 Must use Server table in “ECOM100 Server Client Mapping.PDF” file to see where a Function Code & Modbus memory address maps into DL-PLC memory
# | Slave CPU | Ethernet Port | Device | Function Codes | Memory
1 | Do-more | Internal | @ModbusTCPServer | 1-7, 15, 16, 22 | M-memory
2 |  | ECOM100 | @ECOM_001 | 1-6, 15, 16 | DL-memory1
3 | DL-PLC |  | n/a |  | C, CT, GX, GY, S, SP, T, V, X, Y & Internal ECOM100 memory2

## Slide 28: Communications – Modbus TCP
There are actually 3 Modbus protocols
  (1) Modbus RTU
  (2) Modbus TCP
  (3) Modbus Over TCP
Address
Function Code
Data
Checksum
Modbus RTU Telegram
Modbus TCP Telegram
Transaction Identifier
Protocol Identifier
Length Field
Unit ID
TCP/IP Frame
Do-more & ECOM100s do not natively support Modbus Over TCP
TCP/IP Frame
Address
Function Code
Data
Checksum
Modbus RTU Telegram
Modbus Over TCP is just a Modbus RTU Telegram encapsulated in a TCP/IP Frame
However, it can be accomplished in Do-more using a Custom TCP Device & using the CHECKSUM instruction to calculate the “Checksum” portion of the telegram