## Slide 1: Do-more Technical Training
Hardware

## Slide 2: CPU Hardware
LEDs
  Powered OFF
  All YELLOW: Booter started
  All GREEN: OS started
  YELLOW-RED-GREEN Chase: OS initializing
Notes: - Do power up demonstration

## Slide 3: CPU Hardware
LEDs
  PWR: Power
    OFF – No base power
    GREEN – Base power, battery good
    YELLOW – Base power, battery low

## Slide 4: CPU Hardware
LEDs
  RUN: Run mode
    OFF – Stop (Program) mode
    GREEN – Run mode

## Slide 5: CPU Hardware
LEDs
  ROM: Non-volatile read-only memory (ROM)
    OFF – ROM not being updated
    YELLOW – ROM being updated
Notes: Connect with Do-more Designer
Goto Edit mode in $Main
Add a simple rung
Click <Write PLC> button
Observe ROM light
Make change in Ladder
Press <Write PLC> again
Observe Status bar in Do-more Designer

## Slide 6: CPU Hardware
LEDs
  ERR: Error
    OFF – Normal
    RED
      (1) Fatal error: (e.g. I/O)

## Slide 7: CPU Hardware (ERR LED lit)
Click on Error
Click on Open I/O System View
Notes: While powered up, pull the output module out of the base
Click on the “Error” in the Status Bar
Click on the <Open I/O System View> button
Show progressive detail
Plug module back in
Use PLC  Re-initialize PLC I/O…

## Slide 8: CPU Hardware
LEDs
  ERR: Error
    OFF – Normal
    RED
      Fatal error: (e.g. I/O)
        $IOError (ST152)
        $IOMasterErrors (DST28)
        LocalIOMaster.Slot0_31

## Slide 9: CPU Hardware
LEDs
  ERR: Error
    OFF – Normal
    RED
      (1) Fatal error: (e.g. I/O)
      (2) Software watchdog: PLC scantime greater than $WatchdogTimeVal (DST23)

## Slide 10: CPU Hardware (ERR LED lit)
Click on Error

## Slide 11: CPU Hardware
LEDs
  ERR: Error
    OFF – Normal
    RED
      (1) Fatal error: (e.g. I/O)
      (2) Software watchdog: PLC scantime greater than $WatchdogTimeVal (DST23)
        $WatchdogTimeout (ST128)
Notes: Make a simple C0 to WATCHDOG instruction in $Main selecting “Fire Software Watchdog” as the parameter
Create a Data View with $ScanTime, C0, $WatchdogTimeVal, $WatchdogTimeout in them
Discuss the values & make sure C0 is OFF (use Data View’s Edit mode)
Download to PLC
Put in RUN mode
Turn C0 ON and note response
Turn C0 OFF, clear error and go back to RUN mode

## Slide 12: CPU Hardware
LEDs
  ETH: Ethernet network
    OFF – No connection
    GREEN – Link good
    YELLOW – Activity
Notes: Unplug the Ethernet cable from the built-in port and plug it back in to notice the activity
Notice activity while a link is working

## Slide 13: CPU Hardware
LEDs
  USB: USB activity
    OFF – No activity
    GREEN – Receiving data
    YELLOW – Transmitting data
Notes: Make a USB link with USB cable
Notice activity light

## Slide 14: CPU Hardware
LEDs
  TX: Serial port transmit
    OFF – No activity
    GREEN – Transmitting data
  RX: Serial port receive
    OFF – No activity
    GREEN – Receiving data

## Slide 15: CPU Hardware
LEDs
  All RED: Hardware Watchdog
    Fires if OS stops working for >2 seconds
      $DisableHwWdog (ST25)
        OFF: Enabled
        ON: Disabled
          Disables H/W Watchdog
          Prevents WATCHDOG instruction from working
          Prevents Designer’s Debug Mode from firing H/W Watchdog
      $HwWatchdogMode (ST24)
        OFF: Reboot Mode
          Attempts warm reboot
          Makes entry in System Log
          Sets $WatchdogReboot (ST13)
          Increments $WatchdogReboots (DST385)
            If ≥ 10, CPU stays in Stop (Program) mode
        ON: Shutdown Mode
          No reboots attempted
          Stays in shutdown state

## Slide 16: CPU Hardware
Mode Switch
  RUN: Run
    On power-up, goes to Run mode
  TERM: Terminal; allows Designer to control mode
    On power-up, returns to last mode
  STOP: Stop; Program mode
    On power-up, stays in Stop mode
Designer shows mode switch position
Notes: Flip it and watch the Status Bar

## Slide 17: CPU Hardware
DIP Switches
  0: Load oldest OS
  1: Stay in booter
  2: Disable H/W Watchdog
  3: Disable update (OS/FPGA)
  4: <reserved>
  5: <reserved>
  6: <reserved>
  7: Reset TCP/IP network settings

## Slide 18: CPU Hardware
DIP Switches
  0: Load oldest OS – In case the latest OS failed or features are not wanted, allows reverting to previous version
    (1) Power down
    (2) Remove CPU
    (3) Set DIP #0 ON
    (4) Reinstall CPU
    (5) Power up
  Set DIP #0 OFF to revert to latest OS

## Slide 19: CPU Hardware
DIP Switches
  0: Load oldest OS
Current OS 1.0 (Running)
FW Update
New OS 1.1
New OS 1.1 (Running)
Old OS 1.0 (not running)
New OS 1.1 (not running)
Old OS 1.0 (Running)
Newer OS 1.2 (not running)
Old OS 1.0 (not running)
Newer OS 1.2 (Running)

## Slide 20: CPU Hardware
DIP Switches
  1: Stay in booter – Causes CPU to power up, stay in booter & not run OS
    (1) Power down
    (2) Remove CPU
    (3) Set DIP #1 ON
    (4) Reinstall CPU
    (5) Power up
  Set DIP #1 OFF to power up normally

## Slide 21: CPU Hardware
DIP Switches
  2: Disable H/W Watchdog
    Disables H/W Watchdog
    Prevents WATCHDOG instruction from working
    Prevents Designer’s Debug Mode from firing H/W Watchdog
    (1) Power down
    (2) Remove CPU
    (3) Set DIP #2 ON
    (4) Reinstall CPU
    (5) Power up
  CAUTION: Not recommended!

## Slide 22: CPU Hardware
DIP Switches
  3: Disable update (OS/FPGA): Prevents Designer from being able to update either the OS or the FPGA
    (1) Power down
    (2) Remove CPU
    (3) Set DIP #3 ON
    (4) Reinstall CPU
    (5) Power up

## Slide 23: CPU Hardware
DIP Switches
  7: Reset TCP/IP network settings: Resets back to factory defaults:
    Module ID, Module Name, Module Description, IP Address, Subnet Mask, Gateway Address
    Must be used in conjunction with DIP #1 (Stay in booter)
    (1) Power down
    (2) Remove CPU
    (3) Set DIP #1 & #7 ON
    (4) Reinstall CPU
    (5) Set Mode Switch to TERM
    (6) Power up
    (7) Mode switch: RUN, TERM, RUN, TERM, STOP, TERM, STOP, TERM
    (8) Power down
    (9) Remove CPU
    (10) Set DIP #1 & #7 OFF
    (11) Reinstall CPU
    (12) Power up

## Slide 24: CPU Hardware
DIP Switches
  0-7: Clear All: Clears everything!
    TCP/IP network settings, System Configuration, Memory Configuration, Ladders, Documentation, User Accounts, Passwords
    (1) Power down
    (2) Remove CPU
    (3) Set all DIPs ON
    (4) Reinstall CPU
    (5) Set Mode Switch to TERM
    (6) Power up
    (7) Mode switch: RUN, TERM, RUN, TERM, STOP, TERM, STOP, TERM
    (8) Power down
    (9) Remove CPU
    (10) Set all DIPs OFF
    (11) Reinstall CPU
    (12) Power up

## Slide 25: CPU Hardware
Battery Backup
  3-year life
  CR2032 (P/N: D0-MC-BAT)
  2-hour capacitor
    Holds up memory while replacing battery
  Battery low indications
    PWR light is YELLOW
    $BatteryLow (ST149) = ON
Notes: Power down
Remove battery
Power up & note the color of the PWR light
Create Data View and look at ST149