## Slide 1: Do-more Technical Training
Instruction Set (Analog/Process)

## Slide 2: Instruction Set
THE BASICS
  181 instructions
    Contact (14)
    Coil/Bit Output (11)
    Analog/Process (13)
    Date/Time/Calendar (7)
    Ethernet (5)
    Hardware/Device (9)
    High Speed/CTRIO (19)
    Math (5)
    Misc/Data Manipulation (23)
    Program Control (20)
    Program-Looping (8)
    Protocol-Custom/ASCII (7)
    Protocol-Standard (10)
    String (14)
    Timer/Counter/Drum (16)

## Slide 3: Instruction Set
THE BASICS
  181 instructions
    In-line (100) – no flag
      Executes completely in-line on same scan
    Fully Asynchronous (48) – Red
      Dependent on shared Device’s availability
      Locks Device when executed to make it exclusive
      Unlocks Device after it is finished
      Must not terminate before it is finished
      Must wait for Success or Error indication
    Multi-scan (20) – Yellow
      Takes 2 or more scans to complete or function properly
      Depend on the status of the instruction from previous scan
      (Edge-triggering inputs normally take 2 also)
      ALRATE, FILTER, INTEGRAT, PID, RAMPSOAK, SLOPE, TIMEPROP
    Yielding (5) – Blue
      Can temporarily postpone operation until next scan
    Skipping (6) – Green
      Can skip forward or backward in code
    Yielding/Skipping (2) - Blue Green
      Can temporarily postpone operation until next scan and skip forward or backward in code
Box Instruction
Corner

## Slide 4: Instruction Set (Analog/Process)
Analog/Process
  ALDEV
  ALHILO
  ALRATE
  CLAMP
  DEADBAND
  FILTER
  INTEGRAT
  PID
  PIDINIT
  RAMPSOAK
  SCALE
  SLOPE
  TIMEPROP

## Slide 5: Instruction Set (Analog/Process)
Utilizes Tinker-Toy™ approach
  Other things use common PID controls (Alarms, Ramp/Soak profiles, Filters, Clamping, Deadband, etc.)
  Modular, interchangeable, independent, & run-time configurable
    Using multiple Ramp/Soak profiles for same PID (recipes)
  Easier to troubleshoot
    Filter issue? Deadband too tight? Too wide? Ramp rate in Ramp/Soak too steep? Too slow?
    Right-click on instruction & select Trend Instruction

## Slide 6: Instruction Set (Analog/Process)
ALDEV “Deviation Alarm”
  Sets alarm bits if the input deviates from a set point by more than a limit value
  Parameters:
    Input – location of the monitored value
    Set Point – data value from which the deviation is compared
    Deviation Limit – maximum allowable deviation from the Set Point before an alarm is set
    Positive Alarm (optional) – bit that is set ON if Input > Set Point + Deviation Limit
    Negative Alarm (optional) – bit that is set ON if Input < Set Point – Deviation Limit

## Slide 7: Instruction Set (Analog/Process)
ALHILO “High/Low Alarm”
  Sets various alarm bits based on values
  Parameters:
    Input – location of the monitored value
    High-High Limit – data value for high-high alarm
      High-High Alarm – high-high alarm bit
    High Limit – data value for high alarm
      High Alarm – high alarm bit
    Low Limit – data value for low alarm
      Low Alarm – low alarm bit
    Low-Low Limit – data value for low-low alarm
      Low-Low Alarm – low-low alarm bit
  NOTES:
    All alarm pairs (value/bit) are optional
    Alarms are inclusive
    Alarm values must be consecutive order

## Slide 8: Instruction Set (Analog/Process)
ALRATE “Rate of Change Alarm”
  Sets alarm bits if the input changes at rate faster than a limit value
  Multiscan instruction (yellow triangle)
  Parameters:
    Input – location of the monitored value
    Sample Time – the period (ms) between samples of the Input
    Rate Limit – maximum allowable change of the Input value from one sample time to the next
    Positive Alarm (optional) – bit that is set ON if Input value has increased by more than the Rate Limit since last sample time
    Negative Alarm (optional) – bit that is set ON if Input value has decreased by more than the Rate Limit since last sample time

## Slide 9: Instruction Set (Analog/Process)
CLAMP “Limit Range”
  Constrains a memory location’s highest/lowest value
  Parameters:
    Input – location of the monitored value
    High – maximum allowable value for Input
    Low – minimum allowable value for Input
    Output – location to stored the clamped value

## Slide 10: Instruction Set (Analog/Process)
DEADBAND “Set Outside Deadband”
  Generates an output value only when the input value differs by the deadband value
  Parameters:
    Input – location of the monitored value
    Deadband – minimum change in Input before generating the Output
    Output – location of the new value
  NOTES:
    Deadband value is applied equally above & below

## Slide 11: Instruction Set (Analog/Process)
FILTER “First Order Filter”
  Performs continuous first-order low-pass filtering on input value like a capacitor charging formula:
      where:
        t = time
        τ = tau; the time constant
        e = natural number; 2.71828
      Thus:
        In 1 time constant Out would be about 63% of In
        In 2 time constants Out would be about 86% of In
        In 3 time constants Out would be about 95% of In
        In 4 time constants Out would be about 98% of In
        In 5 time constants Out would be about 99% of In
  Multiscan instruction (yellow triangle)
  Parameters:
    Time Constant – τ in the above equation (in seconds)
    In – location of value to be filtered
    Output – location of filtered value

## Slide 12: Instruction Set (Analog/Process)
INTEGRAT “Integrate over Time”
  Accumulates a value at a time interval:
    Where R0 is calculated once every Sample Time
  Multiscan instruction (yellow triangle)
  Parameters:
    Input – location of data value to integrate
    Sample Time – time interval for the integration
      Constant – hours, minutes, seconds, milliseconds
      Variable – location of time in milliseconds
    Scale Factor – constant value or location of variable value that will be multiplied to the Input
    Integrate Into – location of integral value
  Input Leg:
    EN = Enables integration
    RST = Resets Integrate Into to zero; stops integration

## Slide 13: Instruction Set (Analog/Process)
PID “Closed Loop Controller”
  Proportional, integral & derivative control algorithm
  Multiscan instruction (yellow triangle)
  Parameters:
    PID Struct
    Loop Algorithm:
      Position
      Velocity
    Initialization Mode:
      Set SP equal to PV
      Bumpless

## Slide 14: Instruction Set (Analog/Process)
PID “Closed Loop Controller”
  Parameters (cont’):
    Scale to .PV
      From Raw PV, Raw Min, Raw Max
      Eng. Min, Eng. Max, Eng. Units
    Control Loop
      Forward, Reverse
    Other Options
      Use Error-Squared – less responsive but responds faster with a large error
      Enable Error Deadband – PV more immune to noise
      Disable Bias Freeze – bias keeps changing even if Output go out of range
    Scale from .Output %
      Scaled Min (0%)
      Scaled Max (100%)
      To Scaled

## Slide 15: Instruction Set (Analog/Process)
PID “Closed Loop Controller”
  Input Leg:
    A/M – Automatic / Manual
  Structure (PID)
    <PIDName>: User PID Structure
PID Structure Members (19) |  | 
AutoTuneComp | Gain | Reset
AutoTuning | LastError | SampleTime
AutoTuningErr | Mode | SP
Bias | Output | Tune
DGainLmt | PV | TunedParms
ErrorDB | RanThisScan | TuningAlg
--- | Rate | ---

## Slide 16: Instruction Set (Analog/Process)
PIDINIT “Set PID Tuning Constants”
  Initializes the runtime parameters of a PID loop
  Parameters:
    PID Struct – which PID
    Sample Time – milliseconds
    Gain (P)
    RESET (I)
    Rate (D) – optional

## Slide 17: Instruction Set (Analog/Process)
RAMPSOAK “Ramp Soak Profile”
  Moves a set point through sets of values at prescribed time intervals
  Multiscan instruction (yellow triangle)
  Parameters:
    Ramp/Soak Struct
    Set Point
    Step Preset – which step to begin with
    Action / Value / Time Period / Rate
      INIT TO Value
      SOAK for Constant (or Variable) Time Period
      RAMP to Value
        Over Constant (or Variable) Time Period
        At Rate (per Second, Minute or Hour)
      ADJUST BY Value
        Over Constant (or Variable) Time Period
        At Rate (per Second, Minute or Hour)
  Editing buttons:
    OK, Cancel, Insert, Remove, Move Up, Move Down

## Slide 18: Instruction Set (Analog/Process)
RAMPSOAK “Ramp Soak Profile”
  Input legs:
    E/R – Enable/Reset
    JOG – (edge triggered) moves to next step
    PAU – freezes execution
  Structure (Ramp/Soak)
    <RampSoakName>: User Ramp/Soak Structure
  NOTES:
    Can have up to 50 rows
RampSoak Structure Members (5) |  | 
Done | StepTarget | TimeLeft
Step | StepTime | ---

## Slide 19: Instruction Set (Analog/Process)
SCALE “Scale Value”
  Converts value to engineering units
  Parameters:
    Input – location to be scaled
    In Min – minimum value of Input
    In Max – maximum value of Input
    Out Min – minimum value of Output
    Out Max – maximum value of Output
    Output – location of scaled value

## Slide 20: Instruction Set (Analog/Process)
SLOPE “Calculate Slope”
  Calculates the slope of the line between two points where y is the change in the input value and x is the sample time:
  Multiscan instruction (yellow triangle)
  Parameters:
    Input – location of value to measure slope
    Sample Time – time between samples
    Slope – location of slope value

## Slide 21: Instruction Set (Analog/Process)
TIMEPROP “Time Proportional Control”
  Converts a control output (0-100%) to a pulse-width modulation discrete output control
  Multiscan instruction (yellow triangle)
  Parameters:
    Cycle Time – time period
    Continuous Input – location of input value
    0% Min. Range – minimum value
    100% Max. Range – maximum value
    Discrete Output – output to be cycled

## Slide 22: Instruction Set (Analog/Process)
Process Control Utilities
  PID Overview
  PID View
  Auto-tune Process
  PID Process Simulator

## Slide 23: Instruction Set (Analog/Process)
PID Overview
  PID ref
  Mode
  Ramp/Soak
  Colors
    Green – Auto
    Normal – Manual
    Yellow – Auto-tune
    Red – Alarm
  PV vertical graph
  SP marker
  SP, PV, Bias & Output values
  Output horizontal graph
  Alarm markers
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 24: Instruction Set (Analog/Process)
PID View
  Configuration, tuning & monitoring
  3 panes
    Data form
    PV / SP trend
    Output / Bias trend
Notes: Launchpad: nothing new here
Project Browser:
  Buttons
    Control Logic Filter – Display filter
    New Code Block – Create new code blocks
    Execution Order – Change execution order of blocks
    Status – Shows which blocks are enabled to run
    Sort Code Blocks – Change display order
    Sort Memory – Change display order
  Control Logic
  Configuration
  Tools
Debug View
  NOTE: Message Dump – enables dump to Do-more Logger, $EnableMsgDump (ST36)
Data View
PID Overview

## Slide 25: Instruction Set (Analog/Process)
Auto-tune Process
  Sets optimal values for P, I & D to get ideal response from control system
  Manipulates the PID’s output then measures the rate of change, overshoot and response of the process variable
    Uses Ziegler-Nichols methodology
  Press <Auto-Tune…> button 
  NOTE: 1st make sure process is relatively stable
  Steps:
    Choose which variables to tune
    Choose tuning algorithm
    Decide what to do with newly-tuned PID
    Do something with new tuning constants

## Slide 26: Instruction Set (Analog/Process)
Auto-tune Process (cont’)
  Choose which variables are to be Auto-Tuned (Control Type)
  Choose which type of tuning algorithm to be used (Tuning Algorithm)
    Closed Loop – cycles Output from 0% to 100% & back as PV crosses SP (3 times)
      Choose Deadband around this crossing if necessary
Press <Start Tuning> button… Auto-tune happens…

## Slide 27: Instruction Set (Analog/Process)
Auto-tune Process
  Choose which type of tuning algorithm to be used (Tuning Algorithm)
    Open Loop – Output is bumped & response is measured by the change in PV
      Set Sample Time to 25% of loop’s sample time
      Set Minimum PV Change
      Set Output Bump size
Press <Start Tuning>… Auto-tune happens…

## Slide 28: Instruction Set (Analog/Process)
Auto-tune Process (cont’)
  Decide what to do with the newly-tuned PID
    Return Control to the Ladder Program
    Override Loop Mode as Auto
    Override Loop Mode as Manual
    Recent Tuning History

## Slide 29: Instruction Set (Analog/Process)
Auto-tune Process (cont’)
  Do something with your newly calculated PID constants
    Copy to Clipboard
    Add to PIDINIT Instruction
    Recent Tuning History

## Slide 30: Instruction Set (Analog/Process)
PID Process Simulator
  Do-more Designer has a Virtual PLC (SIM)
  Sim  Setup PID Process Simulator