## Slide 1: Do-more Technical Training
Instruction Set
(Math)

## Slide 2: Instruction Set (Math)
DEC “Decrement”
  Decrements the value in location by 1 every scan as long as it has Power Flow
  Parameters:
    Element – location to decrement
  NOTES:
    Real numbers can also be used

## Slide 3: Instruction Set (Math)
INC “Increment”
  Increments the value in location by 1 every scan as long as it has Power Flow
  Parameters:
    Element – location to decrement
  NOTES:
    Real numbers can also be used

## Slide 4: Instruction Set (Math)
LERP “Linear Interpolation”
  Uses a table of 2 to 50 input / output data pairs to generate an output by interpolation & extrapolation
  Parameters:
    Input Variable – input location
    Output Variable – generated output location
    Output Behavior when Input is Less Than Lowest Input Point
      Clamp to Lowest Output Point
      Extrapolate using Lowest two Points
    Output Behavior when Input in Greater Than Highest Input Point
      Clamp to Highest Output Point
      Extrapolate using Highest two Points
  Editing Buttons
    Insert – inserts row before current row
    Remove – deletes current row
    Move Up – moves current row up
    Move Down – moves current row down
    Sort – orders table by increasing value of the “Input Point” column
    Import – imports data pairs to fill the table from a CSV file
Extrapolate using Highest two Points
x
Clamp to Highest Output Point
Individual Data Point
Linear Interpolation between data points
Individual Data Point

## Slide 5: Instruction Set (Math)
MATH “Calculate Expression”
  Performs complex math in spreadsheet-formula fashion
  8 levels of nested parentheses
  Traditional math precedence:
    Parentheses 
    Exponents (roots)
    Multiplication/Division 
    Addition/Subtraction
      “Please Excuse My Dear Aunt Sally”
  Uses 32-bit math (promotion of bytes, words, dwords)
  Integer math unless reals are involved, then promotion to real math occurs

## Slide 6: Instruction Set (Math)
MATH “Calculate Expression”
Arithmetic Operators | Description | Example
+ | Add | D0 + D1
– | Subtract | D0 – D1
* | Multiply | D0 * D1
/ | Divide | D0 / D1
% | Modulus/Remainder | D0 % D1
** | Raise to Power | D0 ** D1
- | Negate | -D0
+ | 
D0 | 15
D1 | 7
D10 | 22
- | 
D0 | 15
D1 | 7
D10 | 8
* | 
D0 | 15
D1 | 7
D10 | 105
/ | 
D0 | 15
D1 | 7
D10 | 2
% | 
D0 | 15
D1 | 7
D10 | 1
** | 
D0 | 15
D1 | 7
D10 | 170859376
- | 
D0 | 15
D10 | -15

## Slide 7: Instruction Set (Math)
MATH “Calculate Expression”
Binary/Bit-wise Operators | Description | Example
& | Bit-wise AND | D0 & 0x7FFF
¦ | Bit-wise OR | D0 ¦ 0xFFFF
^ | Bit-wise XOR | D0 ^ D1
~ | Bit-wise Invert | ~D0
<< | Shift Left | D0 << 1
>> | Shift Right | D0 >> 1
>>> | Unsigned Shift Right | D0 >>> 1
& | 
D0 | 15 (1111)
D1 | 7 (0111)
D10 | 7 (0111)
¦ | 
D0 | 15 (1111)
D1 | 7 (0111)
D10 | 15 (1111)
^ | 
D0 | 15 (1111)
D1 | 7 (0111)
D10 | 8 (1000)
~ | 
D0 | 15 (0000 000F hex)
D10 | -16 (FFFF FFF0 hex)
<< | 
D0 | 15 (1111)
D1 | 7
D10 | 1920 (0111 1000 0000)
>> | 
D0 | 15 (1111)
D1 | 7
D10 | 0
>>> | 
D0 | 15 (1111)
D1 | 7
D10 | 0
NOTE: Bit positions that have been vacated by the shift are filled with the sign bit
NOTE: Bit positions that have been vacated by the shift are filled with 0 (zero)

## Slide 8: Instruction Set (Math)
MATH “Calculate Expression”
Logical Operators | Description | Example
&& | Logical AND | X0 && X1
¦¦ | Logical OR | X0 ¦¦ X1
! | Logical NOT | !X0
< | Less Than | D0 < D1
<= | Less Than or Equal To | D0 <= D1
== | Equal To | D0 == D1
!= | Not Equal To | D0 != D1
>= | Greater Than or Equal To | D0 >= D1
> | Greater Than | D0 > D1
&& | 
D0 | 15
D1 | 7
D10 | 1
¦¦ | 
D0 | 15
D1 | 7
D10 | 1
NOTE: Are both D0 & D1 non-zero? Yes: D10=1 No: D10=0
NOTE: Is either D0 or D1 non-zero? Yes: D10=1 No: D10=0
! | 
D0 | 15
D10 | 0
< | 
D0 | 15
D1 | 7
D10 | 0
<= | 
D0 | 15
D1 | 7
D10 | 0
== | 
D0 | 15
D1 | 7
D10 | 0
!= | 
D0 | 15
D1 | 7
D10 | 1
>= | 
D0 | 15
D1 | 7
D10 | 1
> | 
D0 | 15
D1 | 7
D10 | 1
NOTE: Is D0 = 0 (zero)? Yes: D10 = 1
No: D10 = 0 (zero)

## Slide 9: Instruction Set (Math)
MATH “Calculate Expression”
Common Functions | Description | Example
ABS | Absolute Value | ABS(D0)
MAX | Maximum Between 2 Expressions | MAX(D0,D1)
MIN | Minimum Between 2 Expressions | MIN(D0,D1)
ABS | 
D0 | 15
D10 | 15
MAX | 
D0 | 15
D1 | 7
D10 | 15
MIN | 
D0 | 15
D1 | 7
D10 | 7

## Slide 10: Instruction Set (Math)
MATH “Calculate Expression”
Real Functions | Description | Example
E | Euler’s Constant e | E()
FRAC | Fractional Portion of Real Number | FRAC(R0)
LN | Natural Log | LN(R0)
LOG | Log Base 10 | LOG(R0)
PI | Returns pi Π (3.14159) | PI()
ROUND | Round Real to Nearest Whole # | ROUND(R0)
SQRT | Square Root | SQRT(R0)
TOINT | Convert to Integer | TOINT(R0)
TOREAL | Convert to Real | TOREAL(D0)
TRUNC | Truncate Real to Whole # | TRUNC(R0)
E | 
R10 | 2.718282
FRAC | 
R0 | 1.234567
R10 | 0.2345670
LN | 
R0 | 1.234567
R10 | 0.2107203
LOG | 
R0 | 1.234567
R10 | 0.09151468
PI | 
R10 | 3.141593
ROUND | 
R0 | 1.234567
R10 | 1.000000
SQRT | 
R0 | 1.234567
R10 | 1.111111
TOINT | 
R0 | 1.234567
D10 | 1
TOREAL | 
D0 | 15
R10 | 15.00000
TRUNC | 
R0 | 1.234567
R10 | 1.000000

## Slide 11: Instruction Set (Math)
MATH “Calculate Expression”
Trig Functions | Description | Example | Result: R10 R0 = 1.234567
ACOS | Arccosine in Radians | ACOS(R0) | ST132 ($OutOfRange) ON Valid Range: -1.0 to +1.0
ASIN | Arcsine in Radians | ASIN(R0) | ST132 ($OutOfRange) ON Valid Range: -1.0 to +1.0
ATAN | Arctangent in Radians | ATAN(R0) | R10 = 0.8899872
COS | Cosine of Radian Angle | COS(R0) | R10 = 0.3299299
DEG | Covert Radians to Degrees | DEG(R0) | R10 = 70.73548
RAD | Convert Degrees to Radians | RAD(R0) | R10 = 0.02154726
SIN | Sine of Radian Angle | SIN(R0) | R10 = 0.9440054
TAN | Tangent of Radian Angle | TAN(R0) | R10 = 2.861231

## Slide 12: Instruction Set (Math)
MATH “Calculate Expression”
Statistical Functions | Description | Example
AVGR | Average of Range of Values | AVGR(R0,10)
MAXR | Maximum Value Across Range | MAXR(R0,10)
MINR | Minimum Value Across Range | MINR(R0,10)
RANDINT | Random Integer (0 – 2147483647) | RANDINT()
RANDREAL | Random Real (0.0 – 1.0) | RANDREAL()
STDEVPR | Population Standard Deviation of Range | STDEVPR(R0,8)
STDEVR | Sample Standard Deviation of Range | STDEVR(R0,8)
SUMR | Sum of Range | SUMR(R0,10)
AVGR(R0,10) R10 = 1.603000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
MAXR(R0,10) R10 = 2.100000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
MINR(R0,10) R10 = 1.200000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
RANDINT & RANDREAL are seeded from the RANDSEED instruction
STDEVPR(R0,10) R10 = 0.3261577 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
STDEVR(R0,10) R10 = 0.3094204 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
SUMR(R0,10) R10 = 16.03000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000

## Slide 13: Instruction Set (Math)
MATH “Calculate Expression”
Conditional Functions | Description | Example
CountIfEQ | Count If Equal | COUNTIFEQ(1.35,R0,10)
CountIfNE | Count If Not Equal | COUNTIFNE(1.35,R0,10)
CountIfGE | Count If Greater Than Or Equal | COUNTIFGE(1.35,R0,10)
CountIfGT | Count If Greater Than | COUNTIFGT(1.35,R0,10)
CountIfLE | Count If Less Than Or Equal | COUNTIFLE(1.35,R0,10)
CountIfLT | Count If Less Than | COUNTIFLT(1.35,R0,10)
IF | If / Else Expression | IF(C7,D0,D1)
SumIfEQ | Sum If Equal | SUMIFEQ(1.35,R0,10)
SumIfNE | Sum If Not Equal | SUMIFNE(1.35,R0,10)
SumIfGE | Sum If Greater Than Or Equal | SUMIFGE(1.35,R0,10)
SumIfGT | Sum If Greater Than | SUMIFGT(1.35,R0,10)
SumIfLE | Sum If Less Than Or Equal | SUMIFLE(1.35,R0,10)
SumIfLT | Sum If Less Than | SUMIFLT(1.35,R0,10)
CountIfEQ(1.35,R0,10) D10 = 1 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
CountIfNE(1.35,R0,10) D10 = 9 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
CountIfGE(1.35,R0,10) D10 = 7 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
CountIfGT(1.35,R0,10) D10 = 6 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
CountIfLE(1.35,R0,10) D10 = 4 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
CountIfLT(1.35,R0,10) D10 = 3 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
If C7 = ON Then D10 = D0 Else D10 = D1
SumIfEQ(1.35,R0,10) R10 = 1.350000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
SumIfNE(1.35,R0,10) R10 = 14.68000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
SumIfGE(1.35,R0,10) R10 = 12.26000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
SumIfGT(1.35,R0,10) R10 = 10.91000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
SumIfLE(1.35,R0,10) R10 = 5.120000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000
SumIfLT(1.35,R0,10) R10 = 3.770000 | 
R0 | 1.200000
R1 | 1.300000
R2 | 2.000000
R3 | 2.100000
R4 | 1.270000
R5 | 1.350000
R6 | 1.750000
R7 | 1.660000
R8 | 1.500000
R9 | 1.900000

## Slide 14: Instruction Set (Math)
MATH “Calculate Expression”
Time Functions | Description | Example
NOW | Get Date/Time 32-bit Integer (1970 Epoch) | NOW()
TICKms | Get Millisecond System Timer Value | TICKms()
TICKus | Get Microsecond System Timer Value | TICKus()
Memory Functions | Description | Example
REF | Read Value Indirectly | REF(D0,V0)
[] | Array Index Expression | D[(V10*16)+V11]
NOW() Returns the number of seconds since 1970
REF(p1,p2) p1: Memory Block Type
(see in Memory Configuration)
p2: Index
D[(V10*16)+V11] D10 = 19473 | 
V10 | 2
V11 | 5
D37 | 19473
REF(p1,p2) similar to REFWRITE “Write Value Indirectly” instruction

## Slide 15: Instruction Set (Math)
RANDSEED “Random Number Seed”
  Sets a seed value that will be used by the RANDINT() “Generate Random Integer” and RANDREAL() “Generate Random Real” functions inside the MATH “Calculate Expression” instruction
  Parameters:
    Seed – location of seed number