## Slide 1: Do-more Technical Training
Instruction Set
(Misc/Data Manipulation)

## Slide 2: Instruction Set (Misc/Data Manipulation)
Picking the Best Instruction

## Slide 3: Instruction Set (Misc/Data Manipulation)
BCDTO “BCD To Integer/Real”
  Converts BCD to integer or real
  Parameters:
    BCD Input – location of BCD value
    Output – location of converted value
  NOTES:
    If BCD Input does not contain valid BCD:
      $OutOfRange (ST132) = ON
      ERR = “Digit greater than 9 in BCDTO…”

## Slide 4: Instruction Set (Misc/Data Manipulation)
TOBCD “Integer/Real To BCD”
  Converts integer or real to BCD
  Parameters:
    Input – location of integer or real number
    BCD Output – location of converted BCD value
  NOTES:
    Only integer portion of real number is converted
    Negative values cannot be converted
      BCD Output = 0 (zero)

## Slide 5: Instruction Set (Misc/Data Manipulation)
DATAINFO “Query Information about Data memory”
  Reads the size or Schema ID of a Data Block or Heap Item
  Parameters:
    Memory Type:
      Data Block – a list of all Data Blocks configured
      Information Type:
        Number of Elements in Block
        Number of BYTEs in Block
        Number of BITs in Block
        Data Type ID (Schema ID)
      Heap Item – a list of all Heap Items configured
      Information Type:
        Number of DWORDs in Heap Item
        Data Type ID (Schema ID)
    Output – location of read value
    Input Leg
      Edge triggered
      Power flow enabled
Schema ID | Description | Schema ID | Description
1 | BIT | 265 | File
2 | Unsigned BYTE | 266 | Program
3 | Signed BYTE | 267 | Device Reference
4 | Unsigned WORD |  | 
5 | Signed WORD | 268 | CTRIO
6 | Signed DWORD | 269 | CTRIO Counter
7 | REAL | 270 | CTRIO Timer
 |  | 271 | CTRIO Pulse Catch
256 | Timer | 272 | CTRIO Pulse
257 | Counter | 273 | CTRIO Discrete
258 | String | 274 | CTRIO Raw
259 | PID |  | 
260 | Clock | 275 | Drum
261 | Task | 276 | Stream
262 | Peerlink | 277 | Server
263 | RampSoak | 278 | Packet
264 | Reserved | 279 | Process Simulator

## Slide 6: Instruction Set (Misc/Data Manipulation)
DECO “Decode to Set Bit”
  Sets a bit (ON) at specified bit position & resets all other bits (OFF)
  Parameters:
    Bit Position Value – location of bit
    Output Bit Pattern – element containing bit
  NOTES:
    If Bit Position Value > 31:
      Output Bit Pattern = 0 (zero)
      $OutOfRange (ST132) = ON
D0 = 0110_0000_0001_0100_0000_0000_0010_1111
“Bit Position Value” = 12
D0 = 0000_0000_0000_0000_0001_0000_0000_0000

## Slide 7: Instruction Set (Misc/Data Manipulation)
ENCO “Encode Bit Position”
  Locates the 1st bit that is ON in memory location
  Parameters:
    Bit Pattern – memory location (up to 32 bits)
    Output Bit Position Value – bit position number
  NOTES:
    If >1 bit is ON, the least significant one is encoded
    If no bits are ON, Output Bit Position Value:
      Signed Dword, Signed Word, Real  -1
      Unsigned Word  65535
      Unsigned Byte  255
D0 = 0000_0011_1000_0010_0000_0000_0000_0000
D1 = 0
These bits are ignored
D1 = 17

## Slide 8: Instruction Set (Misc/Data Manipulation)
GRAY “Gray Code to Integer”
  Converts 16-bit Gray code value to integer
  Parameters:
    Input Value – location to be converted
    Output Value – location of conversion

## Slide 9: Instruction Set (Misc/Data Manipulation)
INIT “Initialize Data”
  Sets each element to specified value
  Parameters:
    Start – location of 1st element in range to be initialized
    End (optional) – location of last element in range to be initialized
    Value – initialization value
  Editing buttons:
    OK – saves & closes editor
    Cancel – discards changes & closes editor
    Insert – inserts empty row before current row
    Remove – deletes current row
    Move Up – moves current row up
    Move Down – moves current row down
  NOTES:
    Can have up to 50 rows

## Slide 10: Instruction Set (Misc/Data Manipulation)
ISCLEAR “Is Structure Cleared”
  Checks if all the members of a particular structure are at their initialized values
    E.g. Is a string empty?
  Parameters:
    Structure – the structure to check
    Set if clear – bit to set ON if structure is clear

## Slide 11: Instruction Set (Misc/Data Manipulation)
MAPIO “Map Inputs/Outputs”
  Intended to map real-world I/O to elements & vice versa
  Parameters:
    Source – input location
    Destination – output location
  Editing buttons:
    OK - saves & closes editor
    Cancel – discards changes & closes editor
    Insert – inserts empty row before current row
    Remove – deletes current row
    Move Up – moves current row up
    Move Down – moves current row down
  NOTES:
    Typically a pair of MAPIO instructions:
      (1) Map real-world inputs  memory
      (2) Map memory  real-world outputs
    Typically use of $tTopOfScan & $tBottomOfScan task code blocks would be used
$tTopOfScan
$tBottomOfScan

## Slide 12: Instruction Set (Misc/Data Manipulation)
MEMCLEAR “Clear Memory”
  Clears a range of memory
  Parameters:
    Start Struct/Numeric – 1st element in range to be cleared
    Number of Elements – number of elements to be cleared

## Slide 13: Instruction Set (Misc/Data Manipulation)
MEMCOPY “Copy Memory Range”
  Copies bytes from one range of memory locations to another without regard to the format of the data
  Parameters:
    Start of Source – location of 1st data byte to be copied
    Start of Destination – location of 1st data byte in destination
    Range – five ways to specify the range
      (1) End of Source – calculates # of bytes of by last location in source
      (2) Number of Source Elements – calculates # of bytes by elements in source
      (3) Number of Bytes – specifies # of bytes
      (4) Number of Destination Elements – calculates # of bytes by elements in destination
      (5) End of Destination – calculates # of bytes by last element in destination
  NOTES:
    Can be used to copy structures

## Slide 14: Instruction Set (Misc/Data Manipulation)
MOVE “Move Value”
  Copies single source value to a single destination
  Parameters:
    Source – value to be copied (constant or variable)
    Destination – location to receive data
  NOTES:
    Copies a structure member, but not entire structures
    If Source & Destination are different types, data conversion is automatically done
    If Source and Destination are different sizes, data may be truncated
D0 = 70000
V0 = 0
V0 = 4464
R0 = 1.234E+08
D1 = 0
D1 = 123400000
CT0.Acc = 451
V0 = 0
V0 = 451

## Slide 15: Instruction Set (Misc/Data Manipulation)
MOVEBIT “Move Single Bit”
  Copies single bit state to a single destination
  Parameters:
    Source Bit – bit to be copied
    Destination – location to receive state
  NOTES:
    Can copy a bit structure member

## Slide 16: Instruction Set (Misc/Data Manipulation)
MOVER “Move Range of Values”
  Copies a range of values to a range of destinations
  Parameters:
    Start of Source – location of 1st value to be copied
    Range – defines the extent of the range
      End of source – end of the source range
      Number of Elements – size of the range
    Start of Destination – location of 1st destination in range
  NOTES:
    Cannot copy structures or their members
    If Source & Destination are different types, data conversion is automatically done
    If Source and Destination are different sizes, data may be truncated

## Slide 17: Instruction Set (Misc/Data Manipulation)
PUBLISH “Translate from Do-more”
  Copies & converts ranges of data from Do-more memory to a data format to be used by external source
  Parameters:
    Source – 1st location to be translated
    Destination – 1st output location
    As – defines format conversion
    # Elements – defines size of range
    Swap Byte – check if needed
    Swap Word – check if needed
  Editing buttons:
    OK - saves & closes editor
    Cancel – discards changes & closes editor
    Edit – edit the current row
    Insert – inserts empty row before current row
    Remove – deletes current row
    Move Up – moves current row up
    Move Down – moves current row down

## Slide 18: Instruction Set (Misc/Data Manipulation)
SUBSCRIB “Translate to Do-more”
  Copies & converts ranges of data used by an external source to Do-more memory
  Parameters:
    Source – 1st location to be translated
    Destination – 1st output location
    As – defines format conversion
    # Elements – defines size of range
    Swap Byte – check if needed
    Swap Word – check if needed
  Editing buttons:
    OK - saves & closes editor
    Cancel – discards changes & closes editor
    Edit – edit the current row
    Insert – inserts empty row before current row
    Remove – deletes current row
    Move Up – moves current row up
    Move Down – moves current row down

## Slide 19: Instruction Set (Misc/Data Manipulation)
REFWRITE “Write Value Indirectly”
  Writes value to location by indirect addressing
  Parameters:
    Value – value to be written
    Reference Type – memory block type
      See in Memory Configuration
      For others, see Help file
    Reference ID – index number of the memory block

## Slide 20: Instruction Set (Misc/Data Manipulation)
ROTL “Rotate Left”
  Rotates bits in location a specified number of bit locations to the left
  Parameters:
    Input/Output – location of bits
    Number of Bits – how many bit locations to shift
  NOTES:
    Most significant bits are looped back to least significant bits
D0 = 0100_0000_1000_0010_0000_0000_0000_0000
D0 = 1000_0001_0000_0100_0000_0000_0000_0000
D0 = 0000_0010_0000_1000_0000_0000_0000_0001
D0 = 0000_0100_0001_0000_0000_0000_0000_0010
D0 = 0000_1000_0010_0000_0000_0000_0000_0100
# of shifts = 0
# of shifts = 1
# of shifts = 2
# of shifts = 3
# of shifts = 4

## Slide 21: Instruction Set (Misc/Data Manipulation)
ROTR “Rotate Right”
  Rotates bits in location a specified number of bit locations to the right
  Parameters:
    Input/Output – location of bits
    Number of Bits – how many bit locations to shift
  NOTES:
    Least significant bits are looped back to most significant bits
D0 = 0000_1000_0010_0000_0000_0000_0000_0100
D0 = 0000_0100_0001_0000_0000_0000_0000_0010
D0 = 0000_0010_0000_1000_0000_0000_0000_0001
D0 = 1000_0001_0000_0100_0000_0000_0000_0000
D0 = 0100_0000_1000_0010_0000_0000_0000_0000
# of shifts = 0
# of shifts = 1
# of shifts = 2
# of shifts = 3
# of shifts = 4

## Slide 22: Instruction Set (Misc/Data Manipulation)
SEG “Hex/BCD to 7 Segment Display”
  Converts 4-digit hex value to 7-segment display
  Parameters:
    4 Digit Hex/BCD Value – location to be converted
    4x8 Bit a-g Output – location of converted value

## Slide 23: Instruction Set (Misc/Data Manipulation)
SETNUMR “Set Numeric Range”
  Sets a range of locations to the same value
  Parameters:
    Start – 1st location of range to be set
    End – last location of range to be set
    Value – value to be written to range

## Slide 24: Instruction Set (Misc/Data Manipulation)
SUMBITS “Sum Bits”
  Counts number of bits in a location that are ON
  Parameters:
    Input Value – location of bits
    Output Sum – value containing number of bits that are ON
D0 = 0100_0000_1000_0010_0000_0000_0000_0000
D1 = 0
1
2
3
D1 = 3

## Slide 25: Instruction Set (Misc/Data Manipulation)
SWAPB “Swap Bytes”
  Swaps bytes and/or words in a range of locations
  Parameters:
    Source – 1st location to be converted
    Destination – 1st location of converted value
    Elements – number of Source locations
    Swap Byte – check if needed
    Swap Word – check if needed
  NOTES:
    Source & Destination don’t have to be same type
Swap Byte, V0  V100 | 
V0 (hex) | V100 (hex)
1234 | 3412
5678 | 7856
ABCD | CDAB
Swap Byte, D0  D100 | 
D0 (hex) | D100 (hex)
12345678 | 34127856
90ABCDEF | AB90EFCD
Swap Word, D0  D100 | 
D0 (hex) | D100 (hex)
12345678 | 56781234
90ABCDEF | CDEF90AB
Swap Byte & Word, D0  D100 | 
D0 (hex) | D100 (hex)
12345678 | 78563412
90ABCDEF | EFCDAB90