## Slide 1: Do-more Technical Training
Module Configuration

## Slide 2: Module Configuration
Module Name: assigned logical name (can be changed)
Type:
  CTRIO/CTRIO2
  ECOM/ECOM100
  ERM/ERM100
  F2-8AD4DA-x
  GS Drive
  SERIO/SERIO4
  Terminator Analog Output
Location: (I/O Master) -> (Base) -> (Slot) or “Disconnected”
“Disconnected”
- Module is missing
- Module type is incorrect If Module is being replaced, this could occur.
(1) Module goes bad
(2) Power down
(3) Remove bad Module
(4) Power up  “Disconnected”
- Allows Module configuration to be saved for replacement Module

## Slide 3: Module Configuration
New Config
  CTRIO/CTRIO2
  ECOM/ECOM100
  ERM/ERM100
  F2-8AD4DA-x
    If 16-bit is chosen:
      Must use WX0:U
  GS Drive
  SERIO/SERIO4
  Terminator Analog Output

## Slide 4: Module Configuration
New Config
Edit Config
  Module type config is pulled up
Delete Config
Delete Disconnected
Assign Config
  Disconnect and kept
  Overwritten

## Slide 5: Module Configuration
Assign Config
Notes: Configure the H2-CTRIO2 as a Counter and Pulse Out
Write program using CTRUNVEL
Confirm it works by Data View & Trend View
Power down
Move CTRIO2 to EBC100 rack
Power up
Configure Ethernet I/O for EBC100
Demonstrate the <Assign Config>, noting no changes were made to the program