## Slide 1: Do-more Technical Training
Programs VS Tasks

## Slide 2: Programs VS Tasks
THE BASICS
  Programs
    Choose a Program if your application requires…
      Timing, or…
      Asynchronous instructions, or…
      Ladder logic needing multiple scans to complete, or…
      Sequential control (Stages)
    Once started (RUN instruction) it runs every scan until:
      Encountering an EXIT instruction
      A HALT instruction in another code block is used to stop it
  Tasks
    Choose a Task if your application requires…
      A single pass through ladder logic executing exactly one time, or…
      Ladder logic that needs to execute at a specific, recurring interval
    Once started (ENTASK instruction) it runs until:
      Execution reaches the last rung
      A HALT instruction in another code block is used to stop it (special case of looping)

## Slide 3: Programs VS Tasks
THE BASICS
  Built-in Programs
    $Main
      Executed every PLC scan while in RUN mode
  Built-in Tasks
    $tFirstScan – only clode block that executes 1 time on STOP-to-RUN transition (before normal scanning starts)
    $tLastScan – last code block that executes on RUN-to-STOP transition
    $tTopOfScan – first code block to execute on each scan
    $tBottomOfScan – last code block to execute on each scan
    $t1Second – after all its ladder logic is executed it schedules itself to run again in 1 second
    $t100ms – <ditto>… in 100ms
    $t50ms - <ditto>… in 50ms
Notes: In $tFirstScan use INIT to initialize V1000-1099 to 5555
In $t1Second use INC to increment D0
In $t100ms use INC to increment D1
In $t50ms use INC to increment D2
In $tTopOfScan use MAPIO to map X0-3 to MI1-4
In $Main use MI1 to turn ON MC1, MI2 to turn ON MC2, MI3  MC3, MI4  MC4
In $BottomOfScan use MAPIO to map MC1-4 to Y0-3
In $tLastScan use INIT to finalize V1000-1009 to 1111
Create Data View:
  V1000-1009
  MI1-4
  MC1-4
  D0-D2
Put in RUN mode
  Notice V1000-1009 goes to 5555
  Notice D0 increments every second, D1 about 10x faster, D2 even faster
  Flip switches and notice Y outputs
Goto PROGRAM mode
  Notice V1000-1009 goes to 1111

## Slide 4: Programs VS Tasks
THE BASICS
  Termination Scan
    Scan which immediately follows the scan in which the Program/Task/Stage was last executed
    Insures proper shutdown
    Insures subsequent startup behavior
    Programs:
      OUT instructions are turned OFF
      Timers & Counters are reset*
      Stages disabled
      Edge bits are turned OFF
    Tasks:
      OUT instructions are turned OFF
      Timers & Counter are reset*
      Edge bits are turned OFF
    Stages:
      OUT instructions are turned OFF
      Timers & Counters are reset*
      Edge bits are turned OFF
      * UDCG “Global Up/Down Counter” & TMRAG “Global Accumulating Timer” are not reset
Notes: Create MyProgram
Copy the code in $Main and put it in MyProgram, add X8 to conditional EXIT
Delete the code in $Main
Create a rung to RUN MyProgram with X5
Download program
Add X0-X7 to Data View
Put Project Browser in Status mode
  Notice $Main, $tBottomOfScan & $tTopOfScan are all running
  Notice MyProgram is not running
    Verify this by flipping X0-3 and no Ys come ON
X5 = ON
  Notice MyProgram is now running
  Flip X0-3 and notice Ys work (leave them ON)
X7 = ON
  Notice all Ys go OFF because MyProgram is exited

## Slide 5: Programs VS Tasks
Edge Bits
  Normally hidden system-only bits
  Internal use only; cannot be modified by user
  Automatically added to project by Do-more Designer as edge-triggered instructions are programmed and assigned an index of zero (/E0)
  Actual usable index value (e.g. “21” of “/E21”) is assigned by the Do-more PLC when project is downloaded (i.e. the PLC, not Do-more Designer, assigns them)
  Holds the scan-to-scan state of edge-triggered inputs
  When an edge is detected (e.g. OFF-to-ON or ON-to-OFF, depending on instruction) the associated Edge Bit is set ON for internal use
Automatic Edge Bit Feature in Stages
  Edge Bits have a special use in Stages due to a desired feature
  When a particular Stage is enabled, if there is an edge-triggered instruction that gets scanned in that stage, the Edge Bit for that instruction is automatically set ON if that input was ON when the Stage was enabled
    Thus what would normally take a minimum of 2-3 scans of that particular Stage to detect an edge for that instruction is actually “detected” (by this feature) on the 1st scan in which that Stage is enabled
S10 Disabled
Rung not scanned
C0 = OFF
S10 Enabled
1
/E0
/E21
2
It took a minimum of 2 scans in order for S10 to “see” C0’s edge. This is normal.
But what if C0 had been ON when S10 was enabled instead of OFF as in this example?
S10 Disabled
S10 Enabled
OFF-to-ON not yet seen because C0 was ON when S10 was enabled
C0 = OFF
OFF-to-ON not yet seen because C0 has just now gone OFF
C0 = ON
3
It took a minimum of 3 scans in order for S10 to “see” C0’s edge.
But this is NOT the way Do-more works!
It only takes 1 scan in order for S10 to “see” C0’s edge if C0 was ON when S10 was enabled. This is because C0’s Edge Bit is automatically set ON as a feature in Do-more
NOTE: This Automatic Edge-Bit Feature is not applied to Counter instructions CNT, CNTDN, UDC or UDCG. These are the ONLY exceptions.

## Slide 6: Programs VS Tasks
Edge Bits
  Since indexes are assigned at download time, Do-more Designer doesn’t “know” what those are until the project is read back up
  All Edge Bits in Do-more Designer originally have an index of zero (e.g. /E0)
  Thus the following two interesting scenarios can occur:
    (1) If a new project with edge-triggered instructions is first saved to disk and then downloaded to the PLC, a dialog will appear describing, “The Program has been modified…” when no manual modification occurred.
      Solution: Save the Project to Disk.
      If Project is not saved to disk then “Modified project not saved to disk – new Edge/Instruction IDs assigned during download to PLC” is displayed in the Output Window as a Warning
    (2) If that project (which was not saved) is closed and then reopened online, the compare will fail.
      If <Compare Programs…> is used the Edge Bit difference is shown
      Solution: Go online with the PLC project and save the project to disk with the new Edge Bit index assignments
/E0
/E21

## Slide 7: Programs VS Tasks
Memory Type
  Structure
    Programs
      $Main
      <Name>
      Structure Members [147]
        Running (bit) – ON if running
        RanThis Scan (bit) – ON if ran this scan
        Done (bit) – ON if completed
        FirstScan (bit) – ON if executing its first scan
        FirstRun (bit) – ON if still executing first full pass
        DoneThisScan (bit) – ON if stopped on current scan
        InstrSuspend (bit) – ON if suspended by SUSPEND instruction
        DebugSuspend (bit) – ON if suspended by a debug operation
        TimeSlice (dword) – microseconds allowed to loop before yielding
        ScanCounter (dword) – number of scans it has run
        RunCounter (dword) – number of times run to completion
        S0_15 (word) – bit/stage indicating enabled/disabled status
        S16_31 (word) – <ditto>
        S32_47 (word) – <ditto>
        S48_63 (word) – <ditto>
        S64_79 (word) – <ditto>
        S80_95 (word) – <ditto>
        S96_111 (word) – <ditto>
        S112_127 (word) – <ditto>
        Sx (bit; x = 0-127) – ON if stage is enabled [128]

## Slide 8: Program VS Tasks
Memory Type
  Structure
    Tasks
      $t1Second, $t50ms, $t100ms, $tBottomOfScan, $tFirstScan, $tTopOfScan
      <Name>
      Structure Members [15]
        Once (bit) – ON if configured to run once
        Continuous (bit) – ON if configured to run continuous
        Running (bit) – ON if running
        RanThisScan (bit) – ON if ran this scan
        Done (bit) – ON if completed
        FirstScan (bit) – ON if executing its first scan
        FirstRun (bit) – ON if still executing first full pass
        DoneThisScan (bit) – ON if will stop on current scan
        InstrSuspend (bit) – ON if suspended by SUSPEND instruction
        DebugSuspend (bit) – ON if suspended by debug operation
        TimeSlice (dword) – microseconds allowed to loop before yielding
        Interval (dword) – how many milliseconds to delay before next run
        ScanCounter (dword) – number of scans it has run
        RunCounter (dword) – number of times run to completion
        IntervalAcc (dword) – how many milliseconds until the next run

## Slide 9: Programs VS Tasks
ADVANCED CONFIGURATION
  Retentiveness
    Definition: code block’s structure members maintain their values through automatic transitions to RUN
      Power cycle
      Restart by Watchdog event
      REBOOT instruction
    Automatic Program-to-Run transition:
      Maintains user code block structure members marked “retentive”
      Maintains System Tasks block structure members (always retentive)
      Exception: $Main’s stages are reset (OFF) & initial stage is set (ON)
      $PgmModeRestart (ST15)  OFF
    Manual Program-to-Run transition:
      Resets all code blocks structure members (even retentive!)
      $PgmModeRestart (ST15)  ON
  NOTE: DTDIFF “Difference Between Two Date/Times” instruction can be used with $SysShutdown (SDT1) & $SysStartup (SDT2) to determine how long PLC has not been in Run mode

## Slide 10: Programs VS Tasks
Enabling & Disabling
Execution Order
Yielding

## Slide 11: Programs VS Tasks (Enabling & Disabling)
FEATURE | Programs | Tasks
Enabled by: | RUN | ENTASK Once on edge Power flow Continuous Interval
Disabled by: | EXIT (internally) HALT (externally) | Reaching last rung (edge ENTASK) Losing power flow HALT (externally; looping Task)
Contain Stages? | Yes | No

## Slide 12
Programs
  $Main is a Program
    Cannot be disabled
    Runs every scan
  Create MyProgram
    Not being scanned
    Edge triggers RUN in $Main
    Now being scanned
    EXIT encountered
    Not being scanned
$Main
MyProgram
MyProgram
Programs VS Tasks (Enabling & Disabling)

## Slide 13
FEATURE | Programs | Tasks
Enabled by: | RUN | ENTASK Once on edge Power flow Continuous Interval
Disabled by: | EXIT (internally) HALT (externally) | Reaching last rung (edge ENTASK) Losing power flow HALT (externally; looping Task)
Contain Stages? | Yes | No
Programs VS Tasks (Enabling & Disabling)

## Slide 14
Programs
  $Main is a Program
    Cannot be disabled
    Runs every scan
  MyProgram created
    Not being scanned
    Edge triggers RUN in $Main
    Now being scanned
    HALT enabled
    Not being scanned
$Main
MyProgram
MyProgram
Programs VS Tasks (Enabling & Disabling)
Notes: In MyProgram, remove the conditional EXIT with X7
In $Main add a conditional HALT of MyProgram with X7
Verify the same behavior

## Slide 15
FEATURE | Programs | Tasks
Enabled by: | RUN | ENTASK Once on edge Power flow Continuous Interval
Disabled by: | EXIT (internally) HALT (externally) | Reaching last rung (edge ENTASK) Losing power flow HALT (externally; looping Task)
Contain Stages? | Yes | No
Programs VS Tasks (Enabling & Disabling)

## Slide 16
Tasks
  $Main is a Program
    Cannot be disabled
    Runs every scan
  Create MyTask
    Not being scanned
    Edge triggers ENTASK
    Scans toward bottom
    Bottom is reached
    Not being scanned
$Main
MyTask
MyTask
Programs VS Tasks (Enabling & Disabling)

## Slide 17
FEATURE | Programs | Tasks
Enabled by: | RUN | ENTASK Once on edge Power flow Continuous Interval
Disabled by: | EXIT (internally) HALT (externally) | Reaching last rung (edge ENTASK) Losing power flow HALT (externally; looping Task)
Contain Stages? | Yes | No
Programs VS Tasks (Enabling & Disabling)

## Slide 18
Tasks
  $Main is a Program
    Cannot be disabled
    Runs every scan
  MyTask created
    Not being scanned
    Power flow to ENTASK
    Now being scanned
    Power flow lost
    Not being scanned
$Main
MyTask
MyTask
Programs VS Tasks (Enabling & Disabling)

## Slide 19
FEATURE | Programs | Tasks
Enabled by: | RUN | ENTASK Once on edge Power flow Continuous Interval
Disabled by: | EXIT (internally) HALT (externally) | Reaching last rung (edge ENTASK) Losing power flow HALT (externally; looping Task)
Contain Stages? | Yes | No
Programs VS Tasks (Enabling & Disabling)

## Slide 20
Tasks
  $Main is a Program
    Cannot be disabled
    Runs every scan
  MyTask created
    Not being scanned
    Power flow to ENTASK
    Scans to bottom
    Bottom is reached
    Power flow remains
    500ms pass
    Scans to bottom again
    Bottom is reached again
    Power flow lost
$Main
MyTask
MyTask
Programs VS Tasks (Enabling & Disabling)

## Slide 21
FEATURE | Programs | Tasks
Enabled by: | RUN | ENTASK Once on edge Power flow Continuous Interval
Disabled by: | EXIT (internally) HALT (externally) | Reaching last rung (edge ENTASK) Losing power flow HALT (externally; looping Task)
Contain Stages? | Yes | No
Programs VS Tasks (Enabling & Disabling)

## Slide 22
Tasks
  $Main is a Program
    Cannot be disabled
    Runs every scan
  MyTask created
    Not being scanned
    Edge triggers ENTASK
    MyTask is looping
      Loop time > .TimeSlice so that MyTask yields
    HALT enabled
    Not being scanned
$Main
MyTask
MyTask
Programs VS Tasks (Enabling & Disabling)

## Slide 23
Create Project w/execution order
8 Examples:
  (1) Program code block $Main
  (2) RUN a succeeding Program
  (3) RUN a preceding Program
  (4) Edge-trig-enable preceding Task
  (5) Edge-trig-enable succeeding Task
  (6) Power-flow-enable succeeding Task
  (7) Power-flow-enable preceding Task
  (8) Program EXIT
$Main
MyTask1
Programs VS Tasks (Execution Order)
MyProgram1
MyTask2
MyTask3
MyProgram2

## Slide 24
(1) Program code block $Main
  1st scan & all subsequent scans if no other Programs or Tasks are enabled
$Main
MyTask1
Programs VS Tasks (Execution Order)
MyProgram1
MyTask2
MyTask3
MyProgram2

## Slide 25
(2) RUN a succeeding Program
  This scan $Main flags MyProgram2 to execute with RUN instruction.
  MyProgram2 executes in the same scan because of the execution order.
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Execution Order)
MyProgram1
MyTask2
MyTask3
MyProgram2
MyProgram2

## Slide 26
(3) RUN a preceding Program
  This scan MyProgram2 flags MyProgram1 to execute with RUN instruction.
  MyProgram1 does not execute in this scan because of the execution order.
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Execution Order)
MyProgram1
MyTask2
MyTask3
MyProgram2
MyProgram1

## Slide 27
(4) Edge-trigger-enable preceding Task
  This scan MyProgram1 flags MyTask1 to execute with ENTASK instruction.
  MyTask1 does not execute in this scan because of the execution order.
  2nd scan after being enabled MyTask1 executes to the bottom and disables itself
  3rd scan after being enabled MyTask1 does not execute
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Execution Order)
MyTask2
MyTask3
MyProgram2
MyProgram1
MyTask1

## Slide 28
(5) Edge-trigger-enable succeeding Task
  This scan MyProgram1 flags MyTask2 to execute with ENTASK instruction.
  MyTask2 executes in this scan because of the execution order.
  MyTask2 executes to the bottom and disables itself
  2nd scan after being enabled MyTask2 does not execute
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Execution Order)
MyTask2
MyTask3
MyProgram2
MyProgram1
MyTask2

## Slide 29
(6) Power-Flow-enable succeeding Task
  This scan MyProgram1 flags MyTask2 to execute with ENTASK instruction.
  MyTask2 executes in this scan because of the execution order.
  MyTask2 continues to execute as long as there is power flow to MyProgram1’s ENTASK
  A subsequent scan MyProgram1 disables ENTASK
  MyTask2 does not execute this scan because of execution order
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Execution Order)
MyTask2
MyTask3
MyProgram2
MyProgram1
MyTask2

## Slide 30
(7) Power-Flow-enable preceding Task
  This scan MyProgram1 flags MyTask1 to execute with ENTASK instruction.
  MyTask1 does not execute this scan because of the execution order.
  2nd scan after being enabled MyTask1 executes because of execution order
  MyTask1 continues to execute as long as there is power flow to MyProgram1’s ENTASK
  A subsequent scan MyProgram1 disables ENTASK
  The next scan after this MyTask1 does not execute.
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Execution Order)
MyTask2
MyTask3
MyProgram2
MyProgram1
MyTask1

## Slide 31
(8) Program EXIT
  This scan MyProgram1 encounters an EXIT instruction and disables itself.
  This scan MyProgram2 also encounters an EXIT instruction and disables itself.
  2nd scan after MyProgram1 and MyProgram2 encounter EXITs they are no longer executing
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Execution Order)
MyTask2
MyTask3
MyProgram2
MyProgram2
MyProgram1
MyProgram1

## Slide 32
Yielding only occurs at “yielding” instructions
Yielding instructions (blue triangle):
  YIELD
  NEXT (w/FOR)
  WEND (w/WHILE)
  UNTIL (w/REPEAT)
  GOTO (if backwards)
Types of yielding:
  (1) Yield every x µsec (default)
  (2) Never yield (except w/YIELD)
  (3) Always yield
Programs VS Tasks (Yielding)

## Slide 33
(1) Yield every 100 µsec (default)
  $Main & MyProgram1 executing
  $Main flags MyTask1 to execute
  MyTask1 executes & reaches WEND
  MyTask1 executing >= .TimeSlice?
    NO. Loop back to WHILE
      Loops until MyTask1 executing >= .TimeSlice
    YES. WEND yields skipping over any logic below the instruction
  MyProgram1 is now scanned.
  Scans until WHILE/WEND is done.
    NOTE: MyTask1 now skips to WEND
  When WHILE/WEND completes, code below WEND is now executed
  MyTask1 disables itself (bottom)
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Yielding)
MyProgram1
MyProgram1
MyTask1
Skipped
Notes: Clear PLC
Create MyTask using 100µs yielding (default)
  Add WHILE X1, INC D0, WEND, INC D1 to MyTask
In $Main add X0  ENTASK MyTask (edge-triggered)
In $tTopOfScan add MATH D2 = TICKus()
In $tBottomOfScan add MATH D3 = TICKus() – D2
Make sure X0 & X1 are OFF & D0-1 = 0
Create Data View with X0-1, D0-1, D3
Use Trend All
Download & put into RUN
Notice D3’s value hovers around 25-30 µs
X0 = ON
  This enables MyTask to run once
  WHILE/WEND doesn’t do anything because X1 = OFF
  D1 increments to 1 for each OFF-to-ON transition of X0 showing MyTask executes the code after the WHILE/WEND but only once
  Notice D3’s value doesn’t change much
X1 = ON
  Nothing happens because MyTask is not executing
Toggle X0 OFF-to-ON
  This enables MyTask to run
  WHILE/WEND is now looping because X1 = ON
  D0 is now incrementing like crazy
  D1 is not incrementing at all showing the code underneath the WHILE/WEND is not executing
  D3 now shows about 135 µsec showing that MyTask’s WHILE/WEND was allowed to loop for 100µs before yielding
X1 = OFF
  WHILE/WEND condition is now gone (X1 = OFF)
  D0 stops incrementing
  D1 increments by 1 indicating after the WHILE/WEND was finished, the code underneath it was executed once
  D3 returns to a value of 25-30 µs
Configure MyTask and change the Yield to 200 µs
Goto Program mode and back to Run (this is necessary to update the new TimeSlice value)
Repeat the experiment noticing the value of D3 now shows 230 µs

## Slide 34
(2) Never yield (except w/YIELD)
  $Main & MyProgram1 executing
  $Main flags MyTask1 to execute
  MyTask1 executes & reaches WEND
  MyTask1 loops until WHILE/WEND is done
    NOTE: WHILE condition must not be I/O or comm dependent
    WARNING: If scantime > $WatchdogTimeVal (DST23) then:
      CPU goes to STOP
      $WatchdogTimeout (ST128) = ON
  Loop completes; code below WEND is executed; scan completes
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Yielding)
MyProgram1
MyProgram1
MyTask1
Notes: Configure MyTask and change to Never Yield
Goto Program mode and back to Run (this is necessary to update the new TimeSlice value)
Repeat the experiment noticing the Do-more watchdogs
Clear Watchdog error

## Slide 35
(3) Always yield
  $Main & MyProgram1 executing
  $Main flags MyTask1 to execute
  MyTask1 executes & reaches WEND
    1st time WEND is reached it does not loop to WHILE
  WEND yields skipping over any logic below the instruction
  Scans until WHILE/WEND is done.
    MyTask1 now skips to WEND
    WEND loops 1 time then yields
  When WHILE/WEND completes, code below WEND is now executed
  MyTask1 disables itself (bottom)
  Subsequent scans
$Main
MyTask1
Programs VS Tasks (Yielding)
MyProgram1
MyTask1
Skipped
Notes: Configure MyTask and change to Always Yield
Goto Program mode and back to Run (this is necessary to update the new TimeSlice value)
Repeat the experiment noticing D0 increments very slowly
Verify the different rate with Trend View