## Slide 1: Do-more Technical Training
Handouts

## Slide 2: Point #1: Device-centric
Hardware or System Resource
Device
Memory
Instruction
Server

## Slide 3: Point #2: Configuration Hierarchy
CPU Configuration
I/O Configuration
Module Configuration(s)
Device Configuration
I/O Mappings
Memory Configuration

## Slide 4: Instruction Set (Misc/Data Manipulation)
Picking the Best Instruction

## Slide 5: Communications – Custom Serial
Custom Protocol | Type | Data Size | Client Instruction | Server Instruction | Server Member
Serial | Stream | Unlimited | STREAMOUT | STREAMIN | InQueue (# of bytes)
 |  |  | STREAMIN | STREAMOUT | 
TCP |  |  | OPENTCP | TCPLISTEN | 
 |  |  | STREAMOUT | STREAMIN | 
 |  |  | STREAMIN | STREAMOUT | 
UDP | Packet | 1 packet | PACKETOUT | PACKETIN | PacketAvailable (bit)

## Slide 6: Communications – DirectLOGIC
# | Master CPU | Ethernet Port | Instruction | Device | Protocol
1 | Do-more | Internal | DLRX/DLWX (Module ID) | @IntEthernet | Broadcast Ethernet II
2 |  |  | DLRX/DLWX (IP Address) |  | UDP
3 |  | ECOM100 | DLRX/DLWX (Module ID) | @ECOM_001 | Broadcast Ethernet II
4 |  | ECOM100 (Peer-to-Peer) |  |  | UDP
5 | DL-PLC | ECOM100 | ECRX/ECWX (Module ID) | n/a | Broadcast Ethernet II
6 |  | ECOM100 (Peer-to-Peer) |  |  | UDP

## Slide 7: Communications – DirectLOGIC
# | Slave CPU | Ethernet Port | Protocol | Device | Memory Available
1 | Do-more | Internal | Broadcast Ethernet II* | @IntEthernet | DL-memory
2 |  |  | UDP |  | 
3 |  | ECOM100 | Broadcast Ethernet II | @ECOM_001 | 
4 |  |  | UDP |  | 
5 | DL-PLC |  | Broadcast Ethernet II | n/a | V, X, Y, C, S, T, CT, GX, GY, SP
6 |  |  | UDP |  | 
* - Currently (as of May-2016) does not work

## Slide 8: Communications – Modbus TCP
# | Master CPU | Ethernet Port | Instruction | Device | Function Codes
1 | Do-more | Internal | MRX/MWX | @IntModTCPClient | 1-7, 15, 16
2 |  | ECOM100 (Modbus TCP Peer-to-Peer) | DLRX/DLWX1 | @ECOM_001 | 1-4, 15, 16
3 | DL-PLC |  | ECRX/ECWX2 | n/a | 
1 Must use Client table in “ECOM100 Server Client Mapping (Do-more).PDF” file to choose correct Function Code & Modbus memory address
2 Must use Client table in “ECOM100 Server Client Mapping.PDF” file to choose correct Function Code & Modbus memory address

## Slide 9: Communications – Modbus TCP
1 Must use Server table in “ECOM100 Server Client Mapping (Do-more).PDF” file to see where a Function Code & Modbus memory address maps into DL-memory
2 Must use Server table in “ECOM100 Server Client Mapping.PDF” file to see where a Function Code & Modbus memory address maps into DL-PLC memory
# | Slave CPU | Ethernet Port | Device | Function Codes | Memory
1 | Do-more | Internal | @ModbusTCPServer | 1-7, 15, 16, 22 | M-memory
2 |  | ECOM100 | @ECOM_001 | 1-6, 15, 16 | DL-memory1
3 | DL-PLC |  | n/a |  | C, CT, GX, GY, S, SP, T, V, X, Y & Internal ECOM100 memory2

## Slide 10: Communications – Modbus TCP
There are actually 3 Modbus protocols
  (1) Modbus RTU
Address
Function Code
Data
Checksum
Modbus RTU Telegram

## Slide 11: Communications – Modbus TCP
There are actually 3 Modbus protocols
  (2) Modbus TCP
Function Code
Data
Modbus TCP Telegram
Transaction Identifier
Protocol Identifier
Length Field
Unit ID
TCP/IP Frame

## Slide 12: Communications – Modbus TCP
There are actually 3 Modbus protocols
  (3) Modbus Over TCP
Do-more & ECOM100s do not natively support Modbus Over TCP
TCP/IP Frame
Address
Function Code
Data
Checksum
Modbus RTU Telegram
Modbus Over TCP is just a Modbus RTU Telegram encapsulated in a TCP/IP Frame
However, it can be accomplished in Do-more using a Custom TCP Device & using the CHECKSUM instruction to calculate the “Checksum” portion of the telegram